## Summ
SCHEDULE OF QUANTITIES
Important Notes: | These preambles apply to all the sections of schedule of quantities and tendered rates shall take into account all these provisions in other parts of the tendered documents:
1 | The Quantities in this schedule are provisional. The Contractor will be paid for the actual quantity of work executed at site at the rates quoted in the tender and finally accepted in writing by the client. The Owner reserves the right to increase or decrease any of the quantities or to totally omit any item or work and any claims by the Contractor in these accounts will not be entertained.
2 | All the items of work given in this schedule of quantities shall be executed strictly in accordance with National Building code of India, ECBC of India & ASHRAE & read in conjunction with the relevant drawings, specifications and the appropriate Indian Standards.
In case of Green Buildings, all the systems & equipment supplied shall meet requirement of IGBC / USGBC/ASHRAE as the case may be, even if not specifically mentioned in the Schedule of Quantities.
3 | The contractor shall visit the site and shall satisfy himself as to conditions under which the wrok is to be performed. No extra claim as a consequence of ignorance or on grounds of insufficient description will be allowed at a later date.
4 | No Alteration whatsoever is to be made to the text or quantities of this schedule of quantities unless alteraion is authorised in writing by client. Any such alterations, notes or additions shall, unless authorised in writing be disregarded when tender documents are considered.
5 | In the event of error occuring to the amount column of the schedule, as a result of wrong extension, unit rate and quantity, the unit rate quoted by the Tenderer and as approved / accepted by the owner shall be regarded as firm and the extension shall be ammended on the basis of the rates.
6 | Any error in totalling in the amount column and in carrying forward totals shall be corrected.
7 | Any error in description or in quantity or omission of items from the contract schedule 'shall not vitiate this contract but shall be corrected and deemed to be a variation required by the owner.
8 | Approved make of materials are listed in "Approved Makes of Material" list and shall have to be adhered to.
```````
9 | All approvals must be obtained from PMC / Owner / Architect before start of the work.
10 | All vendor drawings must be gotten approved from PMC / Owner / Architect / Consultant before fabrication work / site work is started.
11 | All testing and commissioning of equipments and systems shall be done as per relevant IS Standards. All testing records must be submitted properly to Owners / PMC / Architect.
SUMMARY OF COST
SL. NO | DESCRIPTION | AMOUNT (Rs.)
A. | CHILLER PACKAGE INCL. PLANT OPTIMIZER | 0
GRAND TOTAL
Note : | GST SHALL BE EXTRA AS APPLICABLE

## BOQ
GALGOTIA UNIVERSIT, ADMIN BLOCK, GREATER NOIDA
SCHEDULE OF QUANTITIES for AIR-CONDITIONING CHILLER WORKS
Sl. | Description | Unit | Qty. | Rate | Amount
No. |  |  |  | (Rs.) | (Rs.)
Design, Supply, Installation, testing & commissioning of HVAC Installation:
A | SUPPLY OF CHILLERS
1 | Chiller Package - Water Cooled Centrifugal Compressor Chiller with VFD, AHRI Certified
i. | AHRI Certified Water chilling machine with Semi - hermetic / Open type centrifugal compressor, refrigerant / air cooled motor (SPDP), ASME U Stamped / GB Certified flooded insulated chiller, ASME U Stamped / GB Certified water cooled shell & tube condenser, integral refrigerant piping, automatic controls & accessories etc. All mounted on steel frame as per specifications. Motor shall be of high efficiency suitable for 415 ± 10% volts, 50± 3% Hz, 3 phase AC supply. Refrigerant shall be environmentally friendly R134 A. Controls shall be suitable for hookup to BMS, compatible with BacNet / Modbus. Chiller should be capable of unloading from 100 to 20% capacity at constant condenser water temp. conditions without surging & without any hot gas bypass. It should also be stable at constant condeser water temp. condition at Condenser entering water temp. of design condenser entering water temp. + 4°F. (Necessary BMS interface card to be included). Note: Tubes shall be of copper. Tube thickness shall be 0.635 mm at root of fins & 1.2 at plain ends. Necessary vibration isolation pads alongwith necessary foundation nut & bolts to be provided along with the chiller.
Note : Chiller shall be with marine boxes in condenser & evaporator.
VFD & AHF: Chiller shall be with chiller mounted VFD with Active Harmonic Filters to achieve THDI not more than 5% at source at all varying loads. VFD shall be air / water cooled.
a. | Chiller shall come with complete first charge of refrigerant & oil. (Either factory charged/site charged)
b. | Chiller shall have Micro-processor based controls with Graphical/alpha-numeric display in English for all operating parameters such as supply voltage, frequency, load current, chilled water inlet, chilled water outlet, condenser water inlet and outlet temperature & operating pressures etc. Victaulic couplings/ flanged connections at the Chiller / Condenser inlet and outlet shall be supplied along with the chiller package.
c. | Elect. Control Panel
The electrical control panel shall be factory fabricated, unit mounted complete with suitable rated power disconnect switch / MCCB and a VFD with Active Harmonic Filters complete with all safeties, interlocks & protections such as over load, short circuit and single phasing prevention. Main control panel should also display output frequency and voltage to the motor. Note :Central control panel must display VFD readouts as well and provide Bacnet out put for software integration also. Note:- Only 3 phase power supply without neutral shall be available at chiller panel/VFD panel. Neutral if required, for controls / indication lamps shall need to be created by use of suitable control transformer.
The chiller operating parameters shall be :
Chilled water IN : 54ºF (12.22ºC)
Chilled water OUT : 44ºF (6.66ºC)
Chiller Flow Rate : 2.4 GPM/TR
Condenser water IN* 90ºF (32.22ºC)
Condenser water OUT 100ºF (37.77ºC)
Condenser flow rate 3 GPM/ TR
Chiller Fouling Factor 0.0005FPS
Condenser Fouling Factor 0.001FPS
Referigerant R134a
Working Pressure* 150 PSI*
Pressure drop Evaporator : < 8.0 Mtr.
Pressure drop Condenser : < 8.0 Mtr.
COP @ AHRI conditions 6.3
IPLV @ AHRI conditions 0.36
IKW/TR @ Tender conditions at full load 0.65
NPLV @ Tender conditions 0.38
| 1000TR actual capacity @ tender conditions. Water chilling machine as described above and at above mentioned operating conditions. (1W+1S) | Nos. | 2 |  | 0
Note | Chiller shall meet Green Building Norms (Selection Criteria) as per latest relevant ASHRAE Standards. .(TO MEET USGBC/IGBC/GRIHA/ ECBC STANDARDS)
Note | Chiller Supplier / Vendor / Contractor to obtain information from the building Architect /Owners/ PMC about the height / site constraints at the ramp entry & throughout the path of chiller entry in bringing the chiller in the basement plant room. Accordingly, price to be quoted to consider chiller supply in one part, two parts or four parts and then re-assembling at site.
B | INSTALLATION, TESTING & COMMISSIONING OF CHILLERS
1 | Forwarding charges, sea & road freight upto ICD and transit insurance for the above package. | Lot | 1 |  | 0
2 | Clearing the goods at ICD including customs clearance. Loading to the transport vehicle at ICD. Local transport by road including transit insurance. Interaction and clearance at various local points. | Lot | 1 |  | 0
3 | Unloading at site
| Shifting of material to the point of installation using mechanical means (means will be safe & correct method) to the AC Plant Room designated Service Block including by using cranes etc. Chiller vendor / supplier / contractor to find out constraints in bringing the chiller to the designated place before quoting for the job & take into account all the costs required for safe shifting of the chillers in the AC plant Room. | Lot | 1 |  | 0
4 | Insurance for the workmen, material and third party liability. | Lot | 1 |  | 0
5 | Testing & commissioning charges including all consumables. Coordination with Low side HVAC contractor for installation, testing & commissioning activity, technical assistance & trouble shooting etc. | Lot | 1 |  | 0
6 | Comprehensive Annual Maintenance Contract charges for the Chiller packages after the DLP.
a. | First year after DLP | Set | R.O.
b. | Second year after DLP | Set | R.O.
c. | Third year after DLP | Set | R.O.
d. | Fourth year after DLP | Set | R.O.
e. | Fifth year after DLP | Set | R.O.
7 | Any items and works not specifically mentioned above but as required for the works. (Contractor to specify the nature of work / item) | Lot | 1 |  | 0
8 | Control Cabling
Supply and termination laying of required stranded, copper, tined, shielded control cabling between chillers, pumps & valves and chiller plant manager in necessary GI conduiting complete with bends & junction boxes etc.
Wiring Standard
8.1 | 2C x 1.0Sqmm, 1.1 KV grade PVC Insulated, stranded copper conductor, Lead Free armoured FRLS with all accessories for field devices. | RM | 900 |  | 0
8.2 | 3C x 1.5Sqmm, 1.1 KV grade PVC Insulated, stranded copper conductor, Lead Free armoured FRLS cable with all accessories for Powering DDC, Actuators etc. | RM | 400 |  | 0
8.3 | PVC insulated, Twisted Pair, tinned copper conductor CAT-6 cables for BMS / CPO Network. Armoured FRLS as per relevant IS standard. | RM | 200 |  | 0
C | CHILLER PLANT OPTIMIZER
Supply, installation, testing & commissioning of Chiller plant optimizer in a wall mount 16G powder coated, locable sheet steel enclosure. It must combine Bacnet listed 32 bit Supervisory controllers, Bacnet listed 32 bit DDC controllers along with Chiller plant optimization software and logic. This also should be capable to monitor, operate and generate reports from remote location. It should possess 3 tier architecture combination of hardware and software and also must include advance graphics for easy storage and report generation.
Chiller plant manager shall essentially be able to perform the following functions :
1 | Chillers start and stop operation.
2 | Chillers auto sequencing.
3 | Optimizing chillers operation with optimization software and logic.
6 | Auto start and stop of primary variable chilled water pumps.
7 | On and off operation of motorised butterfly valves at chiller outlet.
8 | Having capability for Software integration with Primary chilled water pumps panel.
9 | Having capability to interface with 3rd party BMS system over Bacnet / IP. ON/Off/Trip status of pumps and valves. etc to be available on BMS.( Necessary BMS interface card to be included.)
10 | Having capability to monitor, operate and generate reports from remote location.
Chiller plant manager shall be suitable to manage :
a | 2Nos. Chillers
b | 2Nos.Secondary variable chilled water pumps.
c | 2Nos.Primary fixed chilled water pumps.
d | 2Nos.Tertiary variable chilled water pumps.
e | 2Nos.Cooling Tower.
f | 2Nos.Condenser water pumps.
g | 2Nos. Motorised Chilled water valves.
h | 4Nos. Flow Switches in Evaporator & Condenser outlets of chillers.
i | 8Nos. Temperature Sensors at each Evaporator & Condenser inlet & outlet of each Chiller .
j | 2Nos. Temperature Sensors at CHW header & CDW header .
| Chiller Plant Manager as described above | Set | 1 |  | 0
D. | Non Powered Automatic Tube Cleaning System
a. | Supply, Installation, testing and commissioning of Non Powered Automatic Tube Cleaning System inline to the tender specifications. The ATC system shall operate with only a single motorized ball valve and no other Prime Movers or Electrical/Electronic Components, It shall not require the use of single phase or 3-phase motors to drive any pump, compressor or flow diverter to function. The automatic tube cleaning system operates using difference in water pressure in the cooling water system to circulate the cleaning ball. There should not mix thesupply and return water and shall not have any water loss during operation of ATC. Head Loss should not be greater than 0.4 psi and the power Consumption should not be more that 0.22 kW. The ATC system and all Valves shall be made of stainless steel 304 which is resistant to scaling and able to withstand long term corrosion, should be supplied by the manufacturer. Dedicated System to be installed in every Individual Chiller/Condenser headers based on below parameters : Nos. Of Chillers (1W+1S) : 2 Nos. Maximum Flow rate thru Individual Condenser Header : 3000GPM Pipe Size of Individual Condenser return : 350 mm Refer to the tender specifiactions for more details. | Set | 2 |  | 0
| Total Carried to Summary |  |  |  | 0

## CPM-IO
DATA POINT SUMMARY FOR CHILLER PLANT OPTIMIZER
DI = Digital Input, DO = Digital Output, AI = Analog Input, AO = Analog Output, SW = Software Integration
Sr. No | Description | Qty | Total Points |  |  |  |  | Required signal
A | Water Cooled Screw Chillers | 2 | DI | DO | AI | AO | SW
1 | On/Off command | [5 empty] | 2 | Software Integration signal
2 | Run status | [5 empty] | 2 | Software Integration signal
3 | Trip/Fault/Alarm status | [5 empty] | 2 | Software Integration signal
4 | Auto / Manual status | [5 empty] | 2 | Software Integration signal
5 | CHW Temperature Reset Set point | [5 empty] | 2 | Software Integration signal
6 | Current Limit Setpoint | [5 empty] | 2 | Software Integration signal
7 | CHW Inlet Butterfly (isolation) valve Open/Close command |  |  | 2 |  |  |  | NO/NC Relay Command to Valve
8 | CHW Inlet Butterfly (isolation) valve Open/Close status |  | 2 |  |  |  |  | NO/NC Potential free contact from Valve
9 | Automatic Balancing Valve - Modulation Command |  |  |  |  | 0 |  | 0-10 VDC or 4-20mA to Valve Actuator
10 | Automatic Balancing Valve - Status |  |  |  | 0 |  |  | 0-10 VDC or 4-20mA from Valve Actuator
11 | CDW inlet isolation valve Open/Close command |  |  | 2 |  |  |  | NO/NC Relay Command to Valve
12 | CDW inlet isolation valve Open/Close status |  | 2 |  |  |  |  | NO/NC Potential free contact from Valve
13 | CHW supply & return water temp. at chiller |  |  |  | 4 |  |  | Immersion Temp Sensor (TE-632AM-1+WZ 1000-5)
14 | CDW supply & return water temp. at chiller |  |  |  | 4 |  |  | Immersion Temp Sensor (TE-632AM-1+WZ 1000-5)
15 | Common CHW supply & return header temperature |  |  |  | 4 |  |  | Immersion Temp Sensor (TE-632AM-1+WZ 1000-5)
16 | Common CDW supply & return header temperature |  |  |  | 4 |  |  | Immersion Temp Sensor (TE-632AM-1+WZ 1000-5)
17 | Flow transmitter - Chilled Water Flow |  |  |  | 4 |  |  | 0-10 VDC or 4-20mA from Flow Meter
18 | Flow transmitter - Condenser Water Flow |  |  |  | 4 |  |  | 0-10 VDC or 4-20mA from Flow Meter
19 | Supply/return header Bypass valve command |  |  | 2 |  |  |  | NO/NC Relay Command to Valve
20 | Diff. pressure |  |  |  | 2 |  |  | 0-10VDC from Pressure sensor (P499VAP-105K)
21 | Condenser Tube Cleaning system run status |  | 2 |  |  |  |  | NO/NC Potential free contact from Valve
22 | Side stream Filtration pump run status |  | 2 |  |  |  |  | NO/NC Potential free contact from Valve
23 | Variable Frequency Drive - VFD - Control & Monitoring | [5 empty] | 2 | Software Integration signal
# | Total points |  | 8 | 6 | 26 | 0 | 14
B | Chilled Water Primary Pumps (CHP) | 2 | DI | DO | AI | AO | SW
1 | Pump Auto/Manual status |  | 2 |  |  |  |  | NO/NC Potential free contact from MCC Panel
2 | Pump On/Off command |  |  | 2 |  |  |  | NO/NC Potential free contact from MCC Panel
3 | Pump run status |  | 2 |  |  |  |  | NO/NC Potential free contact from MCC Panel
4 | Pump trip status |  | 2 |  |  |  |  | NO/NC Potential free contact from MCC Panel
# | Total points |  | 6 | 2 | 0 | 0 | 0
C | Chilled Water Secondary Variable Pumps | 2 | DI | DO | AI | AO | SW
1 | Pump Auto/Manual status |  | 2 |  |  |  |  | NO/NC Potential free contact from MCC Panel
2 | Pump On/Off command |  |  | 2 |  |  |  | NO/NC Potential free contact from MCC Panel
3 | Pump run status |  | 2 |  |  |  |  | NO/NC Potential free contact from MCC Panel
4 | Pump trip status |  | 2 |  |  |  |  | NO/NC Potential free contact from MCC Panel
5 | Variable Frequency Drive - VFD - Control & Monitoring | [5 empty] | 2 | Software Integration signal
# | Total points |  | 6 | 2 | 0 | 0 | 2
D | Tertiary Variable Pumps | 2 | DI | DO | AI | AO | SW
1 | Pump Auto/Manual status |  | 2 |  |  |  |  | NO/NC Potential free contact from MCC Panel
2 | Pump On/Off command |  |  | 2 |  |  |  | NO/NC Potential free contact from MCC Panel
3 | Pump run status |  | 2 |  |  |  |  | NO/NC Potential free contact from MCC Panel
4 | Pump trip status |  | 2 |  |  |  |  | NO/NC Potential free contact from MCC Panel
5 | Variable Frequency Drive - VFD - Control & Monitoring | [5 empty] | 2 | Software Integration signal
# | Total points |  | 6 | 2 | 0 | 0 | 2
E | Hot Water Variable Pumps | 2 | DI | DO | AI | AO | SW
1 | Pump Auto/Manual status |  | 2 |  |  |  |  | NO/NC Potential free contact from MCC Panel
2 | Pump On/Off command |  |  | 2 |  |  |  | NO/NC Potential free contact from MCC Panel
3 | Pump run status |  | 2 |  |  |  |  | NO/NC Potential free contact from MCC Panel
4 | Pump trip status |  | 2 |  |  |  |  | NO/NC Potential free contact from MCC Panel
5 | Variable Frequency Drive - VFD - Control & Monitoring | [5 empty] | 2 | Software Integration signal
# | Total points |  | 6 | 2 | 0 | 0 | 2
F | Hot Water Generator | 2 | DI | DO | AI | AO | SW
1 | On/Off command | [5 empty] | 2 | Software Integration signal
2 | Run status | [5 empty] | 2 | Software Integration signal
3 | Trip/Fault/Alarm status | [5 empty] | 2 | Software Integration signal
4 | Auto / Manual status | [5 empty] | 2 | Software Integration signal
5 | HW Temperature Reset Set point | [5 empty] | 2 | Software Integration signal
6 | Current Limit Setpoint | [5 empty] | 2 | Software Integration signal
7 | HW Inlet Butterfly (isolation) valve Open/Close command |  |  | 2 |  |  |  | NO/NC Relay Command to Valve
8 | HW Inlet Butterfly (isolation) valve Open/Close status |  | 2 |  |  |  |  | NO/NC Potential free contact from Valve
9 | HW supply & return water temp. at Hot water |  |  |  | 4 |  |  | Immersion Temp Sensor (TE-632AM-1+WZ 1000-5)
# | Total points |  | 2 | 2 | 4 | 0 | 12
G | Condenser Water Pumps (CDW) | 3 | DI | DO | AI | AO | SW
1 | Pump Auto/Manual status |  | 3 |  |  |  |  | NO/NC Potential free contact from MCC Panel
2 | Pump On/Off command |  |  | 3 |  |  |  | NO/NC Potential free contact from MCC Panel
3 | Pump run status |  | 3 |  |  |  |  | NO/NC Potential free contact from MCC Panel
4 | Pump trip status |  | 3 |  |  |  |  | NO/NC Potential free contact from MCC Panel
# | Total points |  | 9 | 3 | 0 | 0 | 0
H | Colling Tower | 2 | DI | DO | AI | AO | SW
1 | Cooling Tower Auto/Manual status |  | 2 |  |  |  |  | NO/NC Potential free contact from MCC Panel
2 | Cooling Tower On/Off command |  |  | 2 |  |  |  | NO/NC Potential free contact from MCC Panel
3 | Water Level Sensor |  | 2 |  |  |  |  | NO/NC Potential free contact from MCC Panel
4 | Variable Frequency Drive - VFD - Control & Monitoring | [5 empty] | 2 | Software Integration signal
# | Total points |  | 4 | 2 | 0 | 0 | 2
I | Chiller Diagnostic Points | 2 | DI | DO | AI | AO | SW
1 | Leaving chilled liquid - setpoint | [5 empty] | 2 | Software Integration signal
2 | Motor current limit -setpoint | [5 empty] | 2 | Software Integration signal
3 | Leaving chilled liquid - temperature | [5 empty] | 2 | Software Integration signal
4 | Entering chilled liquid - temperature | [5 empty] | 2 | Software Integration signal
5 | Leaving condensor liquid - temperature | [5 empty] | 2 | Software Integration signal
6 | Entering condensor liquid - temperature | [5 empty] | 2 | Software Integration signal
7 | Evaporator pressure | [5 empty] | 2 | Software Integration signal
8 | Condensor pressure | [5 empty] | 2 | Software Integration signal
9 | Oil – low differential pressure | [5 empty] | 2 | Software Integration signal
10 | Motor FLA current | [5 empty] | 2 | Software Integration signal
11 | Discharge pressure | [5 empty] | 2 | Software Integration signal
12 | Operating hours | [5 empty] | 2 | Software Integration signal
13 | Unit safety fault code | [5 empty] | 2 | Software Integration signal
14 | Unit cycling fault code | [5 empty] | 2 | Software Integration signal
15 | Opreation code | [5 empty] | 2 | Software Integration signal
16 | Evaporator – low pressure | [5 empty] | 2 | Software Integration signal
17 | Evaporator – low-pressure – smart freeze | [5 empty] | 2 | Software Integration signal
18 | Evaporator – transducer or leaving liquid probe | [5 empty] | 2 | Software Integration signal
19 | Condenser – high pressure | [5 empty] | 2 | Software Integration signal
20 | Condenser – pressure transducer out of range | [5 empty] | 2 | Software Integration signal
21 | Discharge – low temperature | [5 empty] | 2 | Software Integration signal
22 | Oil – high temperature | [5 empty] | 2 | Software Integration signal
23 | Oil – low differential pressure | [5 empty] | 2 | Software Integration signal
24 | Oil – clogged filter | [5 empty] | 2 | Software Integration signal
25 | Motor controller – loss of current | [5 empty] | 2 | Software Integration signal
26 | Oil – high pressure | [5 empty] | 2 | Software Integration signal
27 | Oil – separator – low level | [5 empty] | 2 | Software Integration signal
28 | Leaving chilled liquid - low temperature | [5 empty] | 2 | Software Integration signal
29 | Motor controller – loss of current | [5 empty] | 2 | Software Integration signal
30 | Sys Oil Temperature | [5 empty] | 2 | Software Integration signal
31 | Sys Oil Pressure | [5 empty] | 2 | Software Integration signal
32 | Sys Oil Filter Pressure | [5 empty] | 2 | Software Integration signal
33 | Slide Valve Position | [5 empty] | 2 | Software Integration signal
34 | Sys Discharge Temp | [5 empty] | 2 | Software Integration signal
35 | System Evaporator Saturation Temperature | [5 empty] | 2 | Software Integration signal
36 | System Evaporator Sub. Temperature | [5 empty] | 2 | Software Integration signal
37 | System Condenser Saturation Temperature | [5 empty] | 2 | Software Integration signal
38 | Evaporator Refrigerant Temperature | [5 empty] | 2 | Software Integration signal
39 | Evaporator Small Temperature Difference | [5 empty] | 2 | Software Integration signal
40 | Condenser Small Temperature Difference | [5 empty] | 2 | Software Integration signal
41 | System Start Times | [5 empty] | 2 | Software Integration signal
42 | Sytem Points depending on Various type & makes of chillers | [5 empty] | 100 | Software Integration signal
# | Total points |  | 0 | 0 | 0 | 0 | 182
J | Base Builder BMS System | 1 | DI | DO | AI | AO | SW
1 | Integration with Base Builder BMS System | [5 empty] | 1 | Software Integration signal
Note- | Please note CPM provided shall be scalabe for future expansion in Plan Room.
| GRAND TOTAL |  | 47 | 21 | 30 | 0 | 217