## BOQ
SCHEDULE OF QUANTITIES
GALGOTIAS UNIVERSITY ADMIN BLOCK
Sl. No. | Description | Unit | Qty | Rate (Rs.) | Amount (Rs.)
A. | BUILDING AUTOMATION SYSTEM
Design, supply, installation, testing and commissioning of Building Management System as follows;
Supply, installation, testing, commissioning & handing over of the following:
1 | BMS Server & Accessories
a. | BMS Computer System: - Xeon Processor (Latest Generation) - 8 GB RAM, 2 TB hard disc -3½” disc drive, DVD writer, compatible CDROM 32” flat screen, 1200 2 800, 256 colours (Full HD) Windows 10 or latest OS and shall have MS-Office installed | Set | 1 |  | 0
2 | Cloud Native BMS Software
a. | Supply, Installation, Testing & Commissioning Cloud Deployed Front end platform with end to end encryption of data points. The package includes licenses, software and platform with in and having SaaS based operations. Future rront end user upgradation, software patches & security updates shall be on the go without any server disruption. Multiple Sites on single dashboard without any latency and simultaneously. Role base (R-Back) Access Control for dashboard users. Over the air On the Go licenses & database updates instantly using agile development methodology, Platfrom shall comprises of Building Portfolio with HVAC Dashboard & Module, | Set | 1 |  | 0
Energy Management Dashboard & Module, Water Management Dashboard & Module, Utility Management Dashboard & Module, Lift Management Dashboard & Module, Fire Alarm System Dashboard & Module. Platform shall have real time Trend Logs with Chart, Bar, Pie, Doughnut & Scattered catagories of selections and reporting capabilities. BI Capabilities shall be integrated and on demand Lock/Unlock facility of module requirements, Shall have P & L, Maintenance modules inbuilt and on demand enablement capable. Platform shall have real time Alarm & Notification and based on the same platform shall have capabilities to provide real time insight for HVAC, Energy, Water, Fire and other services. Inbuilt futurinstic & advance AI & ML enabled forcasting insights without any additional cost. Platform shall capable of user configurations & settings for data points, trends, alarms, etc. setup-ups. Shall have a feature of GUI Casting for each type of solutions & modules.
Cloud Native Storage Server
2.1 | Supply, Installation and Testing & Commissioning of Cloud Deployed Server with on demand auto scalling capabilities using aurchestration tool, 99.95 % uptime-downtime by using distributed architecture and highest level of inbuilt SSL securities and 256 bit encryptions which shall be certified by Digicert, compatible with all type of OS. Shall have machine learning & AI capabilities for Optimization & Energy Savings. Single sign-on for multi site database access through Cloud Based server working independently without any intervention of Local PC based server. Shall have cloud based computing, processing and upgrades shall be on the go without any license upgrade or software changes and without any downtime on server, shall be having cloud data optimization, state of art logic engine, easy to upgrade & change without additional license purchase, highly secured end to end encrypted data transrecieve process with cloud with highest SSL certification. Advanced & future IOT enabled device interface capable. Having all type of anti-virus and also shall be able to share API integration for the high level integration. | Set | 1 |  | 0
3 | Third Party integrator/ Gateway
CE Certified, Wi-Fi-BLE Enabled IOT Device with MQTT Operation Protocol, SSL/TLS Security with End to End data point encryptions, OCP-OVP-UVP-ESD Protections, 12Watt Consumption, 24V DC Supply, Compact Size 166mmx140mmx50mm, Light Weight 410g, Wall & Panel mount two in one plate housing. Length – 166mm Width – 140mm Depth – 45mm without wall mount plate Depth – 50mm with wall mount plate On Board Capabilities Like : 1 x UART 1 x USB debugging 3x 3 Pins connector for RS485 Communication to access data from external device 2x Ethernet - 1 for Internet connectivity purpose Direct Cloud Connectivity Without Supervisory Controller Dependency, Auto Over the Air Software Upgrade without any data desruptions. Topology free architecture having standalone capabilities at all controller level. OPERATING TEMP RANGE 0°C to 65°C STORAGE TEMP RANGE -20°C to 70°C OPERATING HUMIDITY 10%-95% RH (non-condensing) STORAGE HUMIDITY 5%-95% RH (non-condensing)
a. | Chiller Plant Manager | Nos. | 1
b. | Lifts - 8 Nos. | Nos. | 8
c. | Fire Alarm System - Only Monitoring (5000 points X 1 Nos) | Nos. | 1
d. | BTU Meter | Nos. | 1
e. | Solar system renewable energy | Nos. | 1
f. | FCU +Hi Wall Unit Thermostat Integration | Nos. | 24
g. | Water Meters (3 Nos) | Nos. | 3
h. | UPS (5 Nos) | Nos. | 5
i. | DXTYPE PAC | Nos. | 2
j. | PA System | Nos. | 1
k. | Gas sensors for battery room | Nos. | 2
l. | KWH/MFM | Nos. | 25
| Lot for above mentioned systems | Lot | 1 |  | 0
4 | Field DDC Controllers
CE Certified, Wi-Fi-BLE Enabled IOT Device with MQTT Operation Protocol, SSL/TLS Security with End to End data point encryptions, OCP-OVP-UVP-ESD Protections, 12Watt Consumption, 24V DC Supply, Compact Size 166mmx140mmx50mm, Light Weight 410g, Wall & Panel mount two in one plate housing. Length – 166mm Width – 140mm Depth – 45mm without wall mount plate Depth – 50mm with wall mount plate On Board Capabilities Like : 1x 24V DC inputs (2 Pin) 1x (8 pin) 1X8 pins each for Analog Inputs 1x (6 pin) 1X6 pins for each Analog Output, 1x 3 Pins connector for RS485 Communication to access data from external device 1x Ethernet - 1 for Internet connectivity purpose Also, with Auto-Manual Mode, Direct Cloud Connectivity Without Supervisory Controller Dependency, Auto Over the Air Software Upgrade without any data desruptions. Topology free architecture having standalone capabilities at all controller level. OPERATING TEMP RANGE 0°C to 65°C STORAGE TEMP RANGE -20°C to 70°C OPERATING HUMIDITY 10%-95% RH (non-condensing) STORAGE HUMIDITY 5%-95% RH (non-condensing)
CE Certified, Wi-Fi-BLE Enabled IOT Device with MQTT Operation Protocol, SSL/TLS Security with End to End data point encryptions, OCP-OVP-UVP-ESD Protections, 12Watt Consumption, 24V DC Supply, Compact Size 166mmx140mmx50mm, Light Weight 410g, Wall & Panel mount two in one plate housing. Length – 166mm Width – 140mm Depth – 45mm without wall mount plate Depth – 50mm with wall mount plate On Board Capabilities Like : 1x 24V DC inputs (2 Pin) 1x (8 pin) 1X8 pins each for Digital Inputs 1x (6 pin) 1X6 pins for each Digital Output, 1x 3 Pins connector for RS485 Communication to access data from external device 1x Ethernet - 1 for Internet connectivity purpose Also, with Auto-Manual Mode, Direct Cloud Connectivity Without Supervisory Controller Dependency, Auto Over the Air Software Upgrade without any data desruptions. Topology free architecture having standalone capabilities at all controller level. OPERATING TEMP RANGE 0°C to 65°C STORAGE TEMP RANGE -20°C to 70°C OPERATING HUMIDITY 10%-95% RH (non-condensing) STORAGE HUMIDITY 5%-95% RH (non-condensing)
a. | DDC for FM Air Handling Units (upto 2 AHU/ DDC) | Lot | 8 |  | 0
b. | DDC for FM Treated Fresh Air Units (upto 2 AHU/ DDC) | Lot | 1 |  | 0
c. | DDC for Ceiling Suspended Units(2 CSU/DDC) | Lot | 73 |  | 0
c. | DDC for Ceiling Suspended TFA Units(2 CSTFA/DDC) | Lot | 14 |  | 0
f. | DDC for Pressurization Fans (4 Fans/DDC) | Lot | 4 |  | 0
h. | DDC for utility Area Fans(4 Fans/DDC) | Lot | 2 |  | 0
i. | DDC for Smoke Ventilation fan Fans (4 Fans/DDC) | Lot | 4 |  | 0
j. | DDC for Cabinet Fans without VFd (4 Fans/DDC) | Lot | 2 |  | 0
k. | DDC for Fire Fighting System | Lot | 1 |  | 0
l. | DDC for Water Supply System | Lot | 1 |  | 0
m. | DDC for Diesel Generator | Lot | 1 |  | 0
n. | DDC for HT/LT PANEL | Lot | 1 |  | 0
o. | DDC for Lifts - 8 Nos. | Lot | 1 |  | 0
p. | DDC for Motorised Fire Damper | Lot | 1 |  | 0
|  | Total for Above |  |  | 8754290
5 | Networking Switch
5.1 | L2/L3 16 port network switches of suitable specifications to create the desired LAN for IP based DDCs. The specifications and number of the switches shall be calculated based on the design and DDC configuration. All the required accessories, racks etc, shall be included in this line item | Lot | 1 |  | 0
6 | Field Devices
Supply, installation, testing, commissioning of necessary Input sensor transmitters/transducers comprising the following:
b. | Outside Temp & Humidity Sensor with radiation shield. Measuring Range: Temp:-30 to 50 Deg C & RH 0-100%, Accuracy: +/- 1 Degc +/- 3%. | Nos. | 1 |  | 0
c. | Level Switches (Hi/Low). | Nos. | 9 |  | 0
d. | Air DP switch suitable for fan & filter monitoring, NO/NC contact | Nos. | 427 |  | 0
h. | Duct temperature NTC type sensor | Nos. | 164 |  | 0
g. | Duct mount CO2 Sensor, output 0-10 VDC/4-20 mA | Nos. | 16 |  | 0
h. | Duct temperature + Rh sensor 2% acc. 0-10 VDC, NTC/10k RTD | Nos. | 5 |  | 0
i. | Water Pressure Transmitter | Nos. | 3 |  | 0
j | UPS 6 KVA for DDC Power | Nos. | 1 |  | 0
7 | Conduiting , Wiring and cabling
Supply, installation, testing and commissioning of following cables:
7.1 | 2 Core 1.0 Sqmm, unarmoured ATC conductor multistranded, twisted shielded cable for signals and communication | RM | 28465 |  | 0
7.2 | 4 Core 1.0 Sqmm, unarmoured ATC conductor multistranded, twisted shielded cable for signals and communication | RM | 500 |  | 0
7.3 | 3 Core 1.5 Sqmm, unarmoured ATC conductor multistranded, cable for Powering DDC , Actuators. | RM | 1140 |  | 0
7.4 | Cat-6 networking cable | RM | 3990 |  | 0
7.5 | Supplying and laying of following sizes of MS conduit on surface/ recess including cutting/ filling chases along with conduit accessories etc. complete as required.
a. | 25 mm dia | RM | 10035 |  | 0
c. | 20mm dia | RM | 5940 |  | 0
7.6 | MS Flexible conduit of 25mm with end coupler | RM | 3862 |  | 0
| Total Carried to Summary |  |  |  | 8754290
GST SHALL BE EXTRA @ 18% OR AS APPLICABLE.
IMPORTANT NOTES
1 | The offered BMS shall be WEB-BASED system offering Multi-user interface without need of any proprietary BMS software License.
2 | Minimum B-OWS profile, having 5 simultaneous users shall be able to log-in to the BMS WEB-SERVER. The number of users, otherwise, shall be unlimited.
3 | The Offered Web-Server and Embedded Web-Server Engines shall be capable of getting Dynamically Addressed on the DHCP Server.
4 | Number of controllers shall have spare capacity for future expansion up to 10% for each type of IO point and at System Level(Software shall have expansion capacity of 25% IO Points and 25% Software Points)
5 | Wiring of motorized actuator shall be in BMS vendor scope and the power source shall be routed through the respective BMS panel which has UPS power.
6 | System Should be able to integrate with 3D BIM Model.

## IO Summary
GALGOTIA UNIVERSITY ADMIN BLOCK
BMS IO SUMMARY
Sr. No. | Description | Qty. | AI | DI | AO | DO | Soft Point per device | By IBMS Contractor | By 3rd Party Contractors | Outside T/RH sensor | Water Level switch | Air DP switch Air | Duct temperature sensor | Duct mount CO2 Sensor | Wall T+Rh Sensor | Pencil Type Water Pressure Sensor
A | Chiller Plant Manager microprocessor (software) integration for Chiller-intrinsic parameter monitoring including IN/Out CHW Temp, CDW Temp, % Loading, Various Faults and other parameters as per BACnet Point List | [6 empty] | BMS Vendor scope is of soft integrating Chiller plant manager provided by chiller manufacturer. Also chiller and condensor header temperatires to be monitored by BMS vendor by their hardware and sensors. | HVAC Vendor to provide Bacnet over IP interface in Chiller Plant Manager. HVAC Vendor to show the parameters on the software before integrating to IBMS. All mapping details & the Master/slave ID setting in the Chillers to be done by the HVAC Contractor.
1 | Outside T/RH sensor |  | 2 |  |  |  |  | Outside T/RH sensor |  | 1
| Sub Total (A) |  | 2 | 0 | 0 | 0 | 0 |  |  | 1 | 0 | 0 | 0 |  | 0 | 0
B | BMS Computer System: - Xeon Processor (Latest Generation) - 8 GB RAM, 2 TB hard disc -3½” disc drive, DVD writer, compatible CDROM 32” flat screen, 1200 2 800, 256 colours (Full HD) Windows 10 or latest OS and shall have MS-Office installed | 16
1 | ON/OFF Command |  |  |  |  | 16 |  | Potential Free Contact from BMS to AHU Starter panel | Acceptance of Potential Free Output in AHU Panel
2 | Auto / Manual status |  |  | 16 |  |  |  | Potential Free Contact at Auto/Manual Switch | Potential Free Contact in AHU Panel
3 | Supply, Installation, Testing & Commissioning Cloud Deployed Front end platform with end to end encryption of data points. The package includes licenses, software and platform with in and having SaaS based operations. Future rront end user upgradation, software patches & security updates shall be on the go without any server disruption. Multiple Sites on single dashboard without any latency and simultaneously. Role base (R-Back) Access Control for dashboard users. Over the air On the Go licenses & database updates instantly using agile development methodology, Platfrom shall comprises of Building Portfolio with HVAC Dashboard & Module, |  |  | 16 |  |  |  | Differential Pressure Switch across fan | Suitable Insertion Provision in AHU |  |  | 16
Energy Management Dashboard & Module, Water Management Dashboard & Module, Utility Management Dashboard & Module, Lift Management Dashboard & Module, Fire Alarm System Dashboard & Module. Platform shall have real time Trend Logs with Chart, Bar, Pie, Doughnut & Scattered catagories of selections and reporting capabilities. BI Capabilities shall be integrated and on demand Lock/Unlock facility of module requirements, Shall have P & L, Maintenance modules inbuilt and on demand enablement capable. Platform shall have real time Alarm & Notification and based on the same platform shall have capabilities to provide real time insight for HVAC, Energy, Water, Fire and other services. Inbuilt futurinstic & advance AI & ML enabled forcasting insights without any additional cost. Platform shall capable of user configurations & settings for data points, trends, alarms, etc. setup-ups. Shall have a feature of GUI Casting for each type of solutions & modules.
4 | Pre-filter status |  |  | 16 |  |  |  | Differential Pressure Switch across filter | Suitable Insertion Provision in AHU |  |  | 16
5 | Trip status |  |  | 16 |  |  |  | Potential Free Contact from BMS to AHU Starter panel | Potential Free Contact
6 | Return Air Temp |  | 16 |  |  |  |  | Sensor and cabling to DDC panel | Suitable Insertion Provision in duct |  |  |  | 16
7 | AHU Valve Modulation & Feedback |  | 16 |  | 16 |  |  | Cabling to DDC Panel | BMS Compatible valve actuator
8 | Return air CO2 monitoring |  | 16 |  |  |  |  | CO2 Sensor, cabling to DDC Panel | Suitable provision to install CO2 sensor |  |  |  |  | 16
8 | Fresh Air Damper Status & Modulation |  | 16 |  | 16 |  |  | 0-10VDC / 4-20mA Signal,Powering to be provided to actuator | Motorised Damper By HVAC, with acceptance of 0-10 V DC Signal
| Sub Total (B) |  | 64 | 64 | 32 | 16 | 0 |  |  | 0 | 0 | 32 | 16 | 16 | 0 | 0
C | FM TFA | 2
1 | ON/OFF Command |  |  |  |  | 2 |  | Potential Free Contact from BMS to AHU Starter panel | Acceptance of Potential Free Output in AHU Panel
2 | Auto / Manual status |  |  | 2 |  |  |  | Potential Free Contact at Auto/Manual Switch | Potential Free Contact in AHU Panel
3 | Run Status |  |  | 2 |  |  |  | Differential Pressure Switch across fan | Suitable Insertion Provision in AHU |  |  | 2
4 | Pre-filter status |  |  | 2 |  |  |  | Differential Pressure Switch across filter | Suitable Insertion Provision in AHU |  |  | 2
5 | Fine-filter status |  |  | 2 |  |  |  | Differential Pressure Switch across filter | Suitable Insertion Provision in AHU |  |  | 2
6 | Trip Status |  |  | 2 | 2 |  |  | Potential Free Contact from BMS to AHU Starter panel | Potential Free Contact
7 | Supply Air Temp |  | 2 |  |  |  |  | Sensor and cabling to DDC panel | Suitable Insertion Provision in duct |  |  |  | 2
8 | TFA Valve Modulation & Feedback |  | 2 |  | 2 |  |  | Cabling to DDC Panel | BMS Compatible valve actuator
| Sub Total (C) |  | 4 | 10 | 4 | 2 | 0 |  |  | 0 | 0 | 6 | 2 | 0 | 0 | 0
D | Ceiling Suspended AHU | 146
1 | ON/OFF Command |  |  |  |  | 146 |  | Potential Free Contact from BMS to AHU Starter panel | Acceptance of Potential Free Output in AHU Panel
2 | Auto / Manual status |  |  | 146 |  |  |  | Potential Free Contact at Auto/Manual Switch | Potential Free Contact in AHU Panel
3 | Run Status |  |  | 146 |  |  |  | Differential Pressure Switch across fan | Suitable Insertion Provision in AHU |  |  | 146
4 | Trip Status |  |  | 146 |  |  |  | Potential Free Contact from BMS to AHU Starter panel | Potential Free Contact
5 | Pre-filter status |  |  | 146 |  |  |  | Differential Pressure Switch across filter | Suitable Insertion Provision in AHU |  |  | 146
6 | Return Air Temp |  | 146 |  |  |  |  | Sensor and cabling to DDC panel | Suitable Insertion Provision in duct |  |  |  | 146
7 | AHU Valve Modulation & Feedback |  | 146 |  | 146 |  |  | Cabling to DDC Panel | BMS Compatible valve actuator
| Sub Total (D) |  | 292 | 584 | 146 | 146 | 0 |  |  | 0 | 0 | 292 | 146 | 0 | 0 | 0
E | Ceiling Suspended TFA | 28
1 | ON/OFF Command |  |  |  |  | 28 |  | Potential Free Contact from BMS to AHU Starter panel | Acceptance of Potential Free Output in AHU Panel
2 | Auto / Manual status |  |  | 28 |  |  |  | Potential Free Contact at Auto/Manual Switch | Potential Free Contact in AHU Panel
3 | Run Status |  |  | 28 |  |  |  | Differential Pressure Switch across fan | Suitable Insertion Provision in AHU |  |  | 28
4 | Trip Status |  |  | 28 |  |  |  | Potential Free Contact from BMS to AHU Starter panel | Potential Free Contact
5 | Pre+Fine-filter status |  |  | 56 |  |  |  | Differential Pressure Switch across filter | Suitable Insertion Provision in AHU |  |  | 56
7 | TFA Valve Modulation & Feedback |  | 28 |  | 28 |  |  | Cabling to DDC Panel | BMS Compatible valve actuator
| Sub Total (E) |  | 28 | 140 | 28 | 28 | 0 |  |  | 0 | 0 | 84 | 0 | 0 | 0 | 0
F | Pressurization Fans | 13
1 | Fan ON/OFF Command |  |  |  |  | 0
2 | Fan run status |  |  | 13 |  |  |  | Differential Pressure Switch across filter | Suitable Insertion Provision in Fans |  |  | 13
3 | Fan Auto / Manual status |  |  | 13 |  |  |  | Potential Free Contact at Auto/Manual Switch | Potential Free Contact in Panel
| Sub Total (F) |  | 0 | 26 | 0 | 0 | 0 |  |  | 0 | 0 | 13 | 0 | 0 | 0 | 0
G | Utility Area Ventilation Fans | 6
1 | Fan ON/OFF Command |  |  |  |  | 0
2 | Fan run status |  |  | 6 |  |  |  | Potential Free Contact to BMS from Starter panel | Potential Free Contact in fan Panel
3 | Fan Auto / Manual status |  |  | 6 |  |  |  | Potential Free Contact at Auto/Manual Switch | Potential Free Contact in Panel
| Sub Total (G) |  | 0 | 12 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
H | Smoke Ventilation Fans | 15
1 | Fan ON/OFF Command |  |  |  |  | 0 |  | Potential Free Contact from BMS to fan Starter panel | Acceptance of Potential Free Output in Panel
2 | Fan run status |  |  | 15 |  |  |  | Potential Free Contact to BMS from Starter panel | Potential Free Contact in fan Panel
3 | Fan Auto / Manual status |  |  | 15 |  |  |  | Potential Free Contact at Auto/Manual Switch | Potential Free Contact in Panel
| Sub Total (H) |  | 0 | 30 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
I | Cabinet Fans | 5
1 | Fan ON/OFF Command |  |  |  |  | 5 |  | Potential Free Contact from BMS to fan Starter panel | Acceptance of Potential Free Output in Panel
2 | Fan run status |  |  | 5 |  |  |  | Potential Free Contact to BMS from Starter panel | Potential Free Contact in fan Panel
3 | Fan Auto / Manual status |  |  | 5 |  |  |  | Potential Free Contact at Auto/Manual Switch | Potential Free Contact in Panel
| Sub Total (I) |  | 0 | 10 | 0 | 5 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
J | Fire Fighting System
1 | Jockey Pump run status |  |  | 1 |  |  |  | Potential Free Contact at Panel | Potential Free Contact in Panel
2 | Hydrant Pump Run Status |  |  | 1 |  |  |  | Potential Free Contact at Panel | Potential Free Contact in Panel
3 | Fire Pump Run Status (Diesel driven) |  |  | 1 |  |  |  | Potential Free Contact at Panel | Potential Free Contact in Panel
4 | High pressure cut off for sprinkler & hydrant system |  | 1 |  |  |  |  | Pressure Sensor | Provision for sensor installation | [6 empty] | 1
5 | Mid pressure cut off for sprinkler & hydrant system |  | 1 |  |  |  |  | Pressure Sensor | Provision for sensor installation | [6 empty] | 1
6 | Low pressure cut off for sprinkler & hydrant system |  | 1 |  |  |  |  | Pressure Sensor | Provision for sensor installation | [6 empty] | 1
| Sub Total (J) |  | 3 | 3 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 3
K | Water Supply System
1 | Water Tank High / Low Level | 9 |  | 18 |  |  |  | Level Switch | Suitable Insertion Provision |  | 9
2 | Plumbing pumps (WTP -6+ Filter feed -3+Flushing Transfer -3) Run Status | 12 |  | 12 |  |  |  | Potential Free Contact to BMS from fan Starter panel | Potential Free Contact in Pump Panel
3 | Plumbing pumps (WTP -6+ Filter feed -3+Flushing Transfer -3) On/Off Command |  |  |  |  | 12 |  | Potential Free Contact from BMS to fan Starter panel | Acceptance of Potential Free Output in Panel
4 | Plumbing pumps (WTP -6+ Filter feed -3+Flushing Transfer -3) Trip Status |  |  | 12 |  |  |  | Potential Free Contact to BMS from Starter panel | Potential Free Contact in fan Panel
5 | Plumbing pumps (WTP -6+ Filter feed -3+Flushing Transfer -3) Auto / Manual status |  |  | 12 |  |  |  | Potential Free Contact at Auto/Manual Switch | Potential Free Contact in Panel
| Sub Total (K) |  | 0 | 54 | 0 | 12 | 0 |  |  | 0 | 9 | 0 | 0 | 0 | 0 | 0
L | KWH/MFM Metering | 25
1 | KWH / MFM Metering | [5 empty] | 250 | Integrator Unit / Software Connectivity | Meter providing Output on Open Protocol either BACnet / Modbus
| Sub Total (L) |  | 0 | 0 | 0 | 0 | 250 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
M | LT PANEL
1 | LT breaker ON/Off status |  |  | 14 |  |  |  | Potential Free Contact in panel | Potential Free Contact in Panel
2 | LT panel Breaker Trip status |  |  | 14 |  |  |  | Potential Free Contact in panel | Potential Free Contact in Panel
| Sub Total (M) |  | 0 | 28 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
N | Lifts - 8 Nos. | 8
1 | ON/Off status |  |  | 8 |  |  |  | Wiring from Lift Panel | Potential Free Contact in panel
2 | Trip status |  |  | 8 |  |  |  | Wiring from Lift Panel | Hard wire contact in lift controller for tripping in case of fire.
3 | Fireman's Operation mode (auto/manual) status |  |  | 8 |  |  |  | Wiring from Lift Panel | Potential Free Contact in panel
4 | Lift Position |  | 8 |  |  |  |  | 0-10 Vdc from panel | Provision of 0-10 Vdc in lift panel for positioning
5 | Lift Direction |  |  | 8 |  |  |  | Wiring from Lift Panel | Potential Free Contact in panel
6 | Lift Maintenance status |  |  | 8 |  |  |  | Wiring from Lift Panel | Potential Free Contact in panel
| Sub Total (N) |  | 8 | 40 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
O | Motorised Fire Damper | 100
1 | ON/Off status |  |  | 100 |  |  |  | 0-10VDC / 4-20mA Signal,Powering to be provided to actuator | Motorised Damper By HVAC, with acceptance of 0-10 V DC Signal
| Sub Total (O) |  | 0 | 100 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
P | Critical Area T+Rh Monitoring | 5
1 | UPS Room -2 Nos + Server Room -1 Nos+ Mux Room - 1 nos+ Hub Room -1 Nos.) T+Rh Monitoring |  | 10 |  |  |  |  | Wall mount T+Rh Sensor | Provision for Sensor installation | [5 empty] | 5
| Sub Total (P) |  | 10 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 5 | 0
Q | Third Party Integration
1 | Chiller Plant Manager -( Chillers #2nos, & related pumps) | 1 |  |  |  |  | 200 | Integration through either Bacnet over IP / Modbus Protocol | Provision for data communication through either Bacnet over IP / Modbus Protocol
2 | Lifts - 8 Nos. (If provision for this is available then hard point integration will not be done. Decision will be site co-ordinated) | 8 |  |  |  |  | 200 | Integration through either Bacnet over IP / Modbus Protocol | Provision for data communication through either Bacnet over IP / Modbus Protocol
3 | Fire Alarm System - Only Monitoring (5000 points X 1 Nos) | 1 |  |  |  |  | 5000 | Integration through either Bacnet over IP / Modbus Protocol | Provision for data communication through either Bacnet over IP / Modbus Protocol
4 | BTU Meter (1 Nos. ) | 1 |  |  |  |  | 5 | Integration through either Bacnet over IP / Modbus Protocol | Provision for data communication through either Bacnet over IP / Modbus Protocol
5 | Solar system renewable energy | 1 |  |  |  |  | 500 | Integration through either Bacnet over IP / Modbus Protocol | Provision for data communication through either Bacnet over IP / Modbus Protocol
6 | FCU +Hi Wall Unit Thermostat Integration | 24 |  |  |  |  | 120 | Integration through either Bacnet over IP / Modbus Protocol | Provision for data communication through either Bacnet over IP / Modbus Protocol
7 | Water Meters (3 Nos) | 3 |  |  |  |  | 15 | Integration through either Bacnet over IP / Modbus Protocol | Provision for data communication through either Bacnet over IP / Modbus Protocol
8 | UPS (5 Nos) | 5 |  |  |  |  | 100 | Integration through either Bacnet over IP / Modbus Protocol | Provision for data communication through either Bacnet over IP / Modbus Protocol
9 | DXTYPE PAC | 2 |  |  |  |  | 40 | Integration through either Bacnet over IP / Modbus Protocol | Provision for data communication through either Bacnet over IP / Modbus Protocol
10 | PA System | 1 |  |  |  |  | 50 | Integration through either Bacnet over IP / Modbus Protocol | Provision for data communication through either Bacnet over IP / Modbus Protocol
11 | Gas sensors for battery room | 2 |  |  |  |  | 10 | Integration through either Bacnet over IP / Modbus Protocol | Provision for data communication through either Bacnet over IP / Modbus Protocol
| Sub Total (Q) |  | 0 | 0 | 0 | 0 | 6240 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Grand Total (A to Q) |  | 411 | 1101 | 210 | 209 | 6490 |  |  | 1 | 9 | 427 | 164 | 16 | 5 | 3

## DDC Distribution & Sensor (hidden)
Project | Galgotias University
Client | SNC |  |  | Signals |  |  |  |  | Third Party Devices | [6 empty] | Enlite Controllers
S. No. | Equipment Type | DDC Count | Location | AI | DI | AO | DO | RS485 Points | Outside T/RH sensor | Water Level switch | Air DP switch Air | Duct temperature sensor | Duct mount CO2 Sensor | Wall T+Rh Sensor | Pencil Type Water Pressure Sensor | Brdige | Thermo | Infinity
A | Chiller Plant Manager | 1 | Chiller Plant -1 | 2 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
B | AHU Floor Mounted | 8 | Building Floors | 64 | 64 | 32 | 16 | 0 | 0 | 0 | 32 | 16 | 16 | 0 | 0 | 8 | 8 | 0
C | BMS Computer System: - Xeon Processor (Latest Generation) - 8 GB RAM, 2 TB hard disc -3½” disc drive, DVD writer, compatible CDROM 32” flat screen, 1200 2 800, 256 colours (Full HD) Windows 10 or latest OS and shall have MS-Office installed | 1 | Building Floors | 4 | 10 | 4 | 2 | 0 | 0 | 0 | 6 | 2 | 0 | 0 | 0 | 1 | 2 | 0
D | Ceiling Suspended AHU | 73 | Building Floors | 292 | 584 | 146 | 146 | 0 | 0 | 0 | 292 | 146 | 0 | 0 | 0 | 73 | 73 | 0
E | Ceiling Suspended TFA | 14 | Building Floors | 28 | 140 | 28 | 28 | 0 | 0 | 0 | 84 | 0 | 0 | 0 | 0 | 14 | 14 | 0
F | Supply, Installation, Testing & Commissioning Cloud Deployed Front end platform with end to end encryption of data points. The package includes licenses, software and platform with in and having SaaS based operations. Future rront end user upgradation, software patches & security updates shall be on the go without any server disruption. Multiple Sites on single dashboard without any latency and simultaneously. Role base (R-Back) Access Control for dashboard users. Over the air On the Go licenses & database updates instantly using agile development methodology, Platfrom shall comprises of Building Portfolio with HVAC Dashboard & Module, | 3 | Building Floors | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 4 | 0
Energy Management Dashboard & Module, Water Management Dashboard & Module, Utility Management Dashboard & Module, Lift Management Dashboard & Module, Fire Alarm System Dashboard & Module. Platform shall have real time Trend Logs with Chart, Bar, Pie, Doughnut & Scattered catagories of selections and reporting capabilities. BI Capabilities shall be integrated and on demand Lock/Unlock facility of module requirements, Shall have P & L, Maintenance modules inbuilt and on demand enablement capable. Platform shall have real time Alarm & Notification and based on the same platform shall have capabilities to provide real time insight for HVAC, Energy, Water, Fire and other services. Inbuilt futurinstic & advance AI & ML enabled forcasting insights without any additional cost. Platform shall capable of user configurations & settings for data points, trends, alarms, etc. setup-ups. Shall have a feature of GUI Casting for each type of solutions & modules.
G | Utility Area Ventilation Fans | 2 | Utility Area | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0
H | Smoke Ventilation Fans | 4 | Basement Area | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 4 | 0
I | Cabinet Fans | 2 | Building Area | 0 | 10 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0
J | Fire Fighting System | 1 | Basement-1 | 3 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 1 | 1 | 0
K | Water Supply System | 1 | Basement-1 | 0 | 54 | 0 | 12 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0
L | KWH/MFM Metering | 1 | LT Panel | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
M | LT PANEL | 1 | Basement-1 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0
N | Lifts - 8 Nos. | 1 | Terrace | 8 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 5 | 0
O | Motorised Fire Damper | 4 | Basement-1 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0
P | Critical Area T+Rh Monitoring | 1 | UPS Room | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 2 | 0 | 0
Q | Third Party Intgegration (CPM,Lifts, FAS, BTU Solar System,FCU+Hi Wall Unit,Water Meters,UPS,DX Type PAC,PA, GAS Sensors) | 1 | Terrace | 0 | 0 | 0 | 0 | 6240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
| Total | 119 |  | 411 | 1101 | 210 | 209 | 6490 | 1 | 9 | 427 | 164 | 16 | 5 | 3 | 104 | 139 | 2
|  | DDC Count | Signal, Controller, and Sensors Description | DI | DO | AI | AO | RS 485 | Outside T/RH sensor | Water Level switch | Air DP switch Air | Duct temperature sensor | Duct mount CO2 Sensor | Wall T+Rh Sensor | Pencil Type Water Pressure Sensor | Bridge | Thermo | Infinity