## Summary
SUMMARY OF COST
FOR PLUMBING WORKS OF ADMIN BLOCK FOR GALGOTIAS UNIVERSITY AT GREATER NOIDA
S No. | Description | Amount
1 | SANITARY FIXTURES & C.P. FITTINGS (Fixing only) | 0
2 | INTERNAL DRAINAGE (Soil, Waste, Vent, Rain water Pipe & Fittings): | 0
3 | DOMESTIC/ FLUSHING WATER SUPPLY (Internal) | 0
4 | EXTERNAL WATER SUPPLY SYSTEM | 0
5 | GARDEN HYDRANT SYSTEM | 0
6 | EXTERNAL SEWERAGE & DRAINAGE SYSTEM | 0
7 | MISCELLANEOUS ITEMS | 0
8 | PUMPS & PUMP ROOM ACCESSORIES | 0
9 | ELECTRICAL WORKS FOR PLUMBING SYSTEM | 0
| GRAND TOTAL | 0
NOTE: | GST SHALL BE EXTRA AS APPLICABLE
https://drive.google.com/file/d/1xg7oPhAJy71UQzT3S1fDp6gjf_57DQfE/view?usp=sharing
Link for Water Schematic
https://drive.google.com/file/d/1vOymHLeZxxCRFAXZ3OAfltiNRvnisv2u/view?usp=sharing
Link for Plumbing & FF Drawings Floor Plan

## BOQ
SCHEDULE OF QUANTITIES
FOR PLUMBING WORKS OF ADMIN BLOCK FOR GALGOTIAS UNIVERSITY AT GREATER NOIDA
PREAMBLE
| 1 | All items of work under this Contract shall be executed strictly to fulfill the requirements laid down under “Basis of Design” in the specifications. Type of equipment, material specification, methods of installation and testing and type of control shall be in accordance with the specifications, approved shop drawings and the relevant Indian Standards, however capacity of each component and their quantities shall be such as to fulfill the above mentioned requirement.
| 2 | The unit rate for all equipment or materials shall include cost in INDIAN RUPEES (INR) for equipment and materials including all taxes and duties and also including forwarding, freight, insurance and transport,loading unloading, housekeeping, safety and security into Contractor’s store at site, storage, installation, testing, balancing, commissioning and other works required.
| 3 | The rate for each item of work included in the Schedule of Quantities shall, unless expressly stated otherwise, include cost of:
a. All materials, fixing materials, accessories, appliances tools, plants, equipment, transport, labour and incidentals required in preparation for and in the full and entire execution, testing, balancing, commissioning and completion of work called for in the item and as per Specifications and Drawings.
b. Wastage on materials and labour.
c. Loading, transporting, unloading, handling/double handling, hoisting to all levels, setting, fitting and fixing in position, protecting, disposal of debris and all other labour necessary in and for the full and entire execution and for the job in accordance with the contract documents, good practice and recognized principles.
d. Liabilities, obligations and risks arising out of Conditions of Contract.
e. All requirements of Specifications, whether such requirements are mentioned in the item or not. The Specifications and Drawings where available, are to be read as complimentary to and part of the Bill of Quantities and any work called for in one shall be taken as required for all.
f. In the event of conflict between Bill of Quantities and other documents including the Specifications, the most stringent shall apply. The interpretation of the Architect / Consultant /Project Manager shall be final and binding.
| 4 | The Contractor shall procure and bring Materials/Equipment to the site only on the basis of drawings approved for construction and shop drawings and not on the basis of Bill of Quantities which are approximate only. This also applies to the Contractor’s requisition for Owner supplied materials. Quantity indicated in BOQ are estimated quantity. Vendor / Contractor carry out the actual measurement at site and submit schedule to take permission from PMC / Client Project Manager before procurement. This contract will be operated on unit rate basis and payment shall be made as per actual erected quantity at site.
| 5 | The contractor shall include for making all the opening in slabs, beams, walls etc. as required for his work. However, the contractor can coordinate with civil work to provide necessary sleeves. All openings shall be closed using water proofing compound or as specified by Project Manager. G.I. pipe sleeve of suitable higher size shall be provided wherever the pipes are crossing the walls/floors and sealing the sleeves with glass wool in between & fire sealant compound at either end.
| 6 | The work shall be carried out in conformity with the plumbing drawings and within the requirements of architectural, HVAC, electrical structural and other specialized services drawings.
| 7 | The contractor shall cooperate with all trades and agencies working on the site. He shall make provision for hangers, sleeves, structural openings and other requirements well in advance to prevent hold up of progress of the construction schedule. All supports to the civil structure shall be provided with anchor fastners.
| 8 | On award of the work, contractor shall submit a schedule of construction in the form of a PERT chart or BAR chart for approval of the Project Manager. Along with schedule contractor to submit Project Team and their hierarchy chart, cash flow, shop drawing submittal and approval schedule, equipments and material technical data sheet schedule, material delivery schedule, manopower deployment schedule.
| 9 | On award of the work the contractor shall be issued two (2) sets of consultant’s drawings. The drawings shall be the basis of contractor’s shop drawings.
| 10 | Shop drawings are detailed working drawings coordinated with other trading work, which incorporate the contractor’s details for execution of the work and incorporate equipment manufacturer’s details and dimensions to ensure that the same can be installed in the space provided.
| 11 | All shop drawings should detail pipe routing and levels, showing location of other services at crossings etc., cable runs, route cable trays and all allied works and must be fully coordinated with other services, before execution of the works.
| 12 | All shop drawings will be made on Autocad and coloured prints has to be produced for site work.
| 13 | All rates quoted are inclusive of cutting holes and chases in walls and floors with core cutting machines ans electrical chasing machines and making good the same with cement mortar / concrete / water proofing of appropriate mix and strength as directed by the Project Manager. Contractor shall provide holes, sleeves, recesses in the concrete and masonry work as the work proceeds. All hot and cold water supply pipes crossing masonry walls of typical guest room toilets shall be provided with GI pipe sleeves. The annular space between the pipe and sleeve shall be filled up with glass wool in between and fire proof sealent on either end after testing.
| 14 | Any pipe crossing fire rated wall as per fire compartmentation will be provide with higher size of GI sleeve. All floor crossing pipes will be provided with higher size GI sleeve.
| 15 | The contractor shall , from time to time, clear away all debris and excess materials accumulated at the site failing which the same shall be done by Project Manager at contractor’s risk and cost and cost of clean up shall be deducted from the contractors prorata bill.
| 16 | After the fixtures, equipment and appliances have been installed and commissioned, contractor shall cleanup the same and remove all plaster, paints, stains, stickers and other foreign matter or discoloration leaving the same in a ready to use condition.
| 17 | On completion of all works, contractor shall demolish all stores, remove all surplus materials and leave the site in a broom clean condition, failing which the same shall be done by the Project Manager at the Contractor'’ risk and cost. Cost of the cleanup shall be deducted from the contractor’s bills on pro-rata basis in proportion to his contact value.
| 18 | Contractor shall furnish sample of materials such as pipe, union, elbow, support (angle, hanger, rod, etc.), fittings, accesssories, sealant, cable trays, switches, sockets, etc. proposed for the project for Engineer's / PMC / Project Manager / Architect's approval before procurement / installation.
| 19 | The Contractor / Tenderer should quote rates based on the first approved make of each item in the List of Approved Makes attached with the technical specifications of this tenderer OR specify the make which is quoted.
| 20 | The rates quoted shall also include submission and approval of shop drawings, As-built drawings, Technical Data Sheet, Inspection, factory inspection,Testing and Commissioning
| 21 | Rate should include to follow Client / Godrej compliances such as Safety, Security of vendor store and material, regular housekeeping, etc. Dedicate resource to consider.
| 22 | Contractor shall list here any other items not included but necessary for the complete and satisfactory completion of each section of the work. Such items shall deemed to be included in other rates unless specifically listed here.
| S. No. | Description | Unit | Total Qty. | Rate (Rs.) | Amount (Rs.)
| 1 | SANITARY FIXTURES & C.P. FITTINGS (Fixing only)
Note:-
Sizes of all Sanitary fixtures given are for identification purpose only and may vary depending on the makes & models as per final approval of Architect / Client. No extra cost shall be paid for the same. All Vitreous china sanitary wares, Accessories, Bath tubs, Kitchen sinks, , C.P. brass fittings & accessories as per Annexure I will be supplied free of cost to the contractor at site. The supply will be made by the manufacturer/ Vendors as standard supply. Contractor will include providing and fixing of all other accessories like CI Chair brackets, Angle iron frames, extension piece, copper pipe for fixtures connection, nuts, bolts, washers, teflon tape etc. any other device / accessories to complete the work under respective items for the same in the tender. No extra payment on this account shall be made as per Annexure 1.
In the items below selection of the model shall be made by the Client/Architect as they reserve the right to specify any of the model in the approved list.
EWC
| 1.01 (a) | Receiving, Unloading, Storing, transporting, testing & Commissioning wall hung /Floor mounted type white vitreous china European water closet with concealed `P' or ‘S’ trap, seat & lid (heavy duty) C.P. brass hinges, including C.I. chair, with chair grouting, rubber buffers, C.P. nuts, bolts, etc. including PVC connector pipe from P or S trap with rubber bush, accessories CI / MS brackets painted with two coats of approved shade over a coat of primer, C.P. Brass screws and wooden cleats, including cutting and making good the walls & floors wherever required. | Each | 138
WB
| 1.02 (a) | Receiving, Unloading, Storing, transporting, testing & Commissioning of Exposed/concealed in wall flushing cisterns with dual flushing actuator plate ( plastic body in approved finish ), flush stop function noise less float valve and fast filling action with all component parts of high quality complete in all respects. | Each | 138
URINAL | 1.03 (a) | Receiving, Unloading, storing, transporting, testing & Commissioning white glazed vitreous China wash basin (under / over the counter) with 32 mm dia C.P brass waste of standard pattern, 32 mm dia C.P cast brass bottle trap and union, 32 mm dia C.P brass pipe to wall and CP wall flange, and rubber acceptors for waste connection, R.S. or C.I. painted brackets bolts, nuts etc. cutting & making good the wall and floor wherever required. Gap shall be filled with silicon sealant where ever required including all accessories require to complete the installation.
|  | Oval / round wash basin/Flat back wash basin, Wash Basin Size & color as per Archtect and Client | Each | 166
| 1.04 (a) | Receiving, Unloading, storing, transporting, testing & Commissioning of 15mm dia C.P. pillar tap for wash basin complete including cutting and making good the walls wherever required including all accessories require to complete the installation. (For Typical Toilets ground to 19M) | Each | 166
| 1.05 (a) | Receiving, Unloading, Storing, transporting, testing & Commissioning white glazed vitreous china large flat back lipped front urinal basin, C.I bracket (white colour painted) 40 mm CP brass domical waste, 40 mm C.P. caste brass bottle trap, CP flush pipe with spreader & other necessary fittings including C.P. brass hex nipple; elbow; unions, washers, cap, C.P. nuts, bolts etc making holes in walls, floors & making good. (For Typical Toilets ground to 19M)
|  | Urinal - Flat back lipped frontal, Size & color as per Archtect and Client. | Each | 60
SOAP DISP. | 1.06 (a) | Receiving, Unloading, Storing, transporting, testing & Commissioning Infra-Red based electronic urinal flushing system electrical / 6V DC (4AA) battery operated for urinals comprising of solenoid valve, concealed built in strainer & flow mechanism piping, flush mounted sensors with all accessories & fittings complete in all respect in fully operational condition etc including cutting and making good the wall where required. (For Typical Toilets ground to 19M) | Each | 60
ABLUTION | 1.07 | Receiving, Unloading, Storing, transporting, testing & Commissioning white glazed vitreous china urinal partitions of approved make including rawl plugs, screws or any other approved device for Fixing arrangements, making holes in walls, floors & making good.
| a) | Size 680 mm x 300 mm. | Each | 60
HC Toilet
| 1.08 | Receiving, Unloading, Storing, transporting, testing & Commissioning Stainless steel kitchen sink with R.S. or CI bracket (painted white), 40 mm dia C.P. brass waste of standard pattern, C.P. brass chain and rubber, 40 mm dia caste brass bottle trap with necessary union, C.P. pipe to wall & CP wall flange complete with cutting and making good the walls where required Including all accessories require to fix the sink in granite or given platform and sealing side for leak proof complete.
HC Toilet | a) | Single bowl with single drain board. | Each | 9
RO Water cooler | 1.09 | Receiving, Unloading, Storing, transporting, testing & Commissioning Wall Mounted C.P. Brass Long Nose swinging casted spout of required size including cutting and making good the wall wherever required. | Each | 9
| 1.1 | Receiving, Unloading, Storing, transporting, testing & Commissioning of C. P. Brass single lever concealed Shower mixer 15 mm C.P brass spout & wall flange (for shower) including necessary fittings/ accessories, cutting & making good the wall wherever required. (For Other areas Toilets of Basements ground & L-1) | Each | 2
| 1.11 | Receiving, Unloading, Storing, transporting, testing & Commissioning of revolving type shower head & shower arm (discharging multiple type of sets) including cutting and making good the walls / floors wherever required. (For Other areas Toilets of Basements ground & L-1)
| a) | 1 No. Shower Head | Each | 2
| b) | 1 No. shower arm incl. necessary fittings/accessories, cutting and making good the wall . | Each | 2
| 1.12 | Receiving, Unloading, Storing, transporting, testing & Commissioning of stainless steel toilet paper holder of approved makes. Including cutting hole in the masonry/R.C.C wall and making good with cement mortar.
| a) | Size 150 mm x 150 mm | Each | 138
| 1.13 | Receiving, Unloading, Storing, transporting, testing & Commissioning of CP brass coat hooks (double) of approved make. Including providing & fixing C.P brass screws, washers, rawl plug etc. | Each | 138
| 1.14 | Receiving, Unloading, Storing, transporting, testing & Commissioning of liquid soap dispenser of approved make. Including screws, washers and rawl plug etc. | Each | 83
| 1.15 | Receiving, Unloading, Storing, transporting, testing & Commissioning of CP brass short/long body bib cock including, necessary flange, cutting and making good he walls / floors wherever required complete. (For JC and Other areas) | Each | 9
| 1.16 | Receiving, Unloading, Storing, transporting, testing & Commissioning of 15 mm dia C. P. Brass angle valve with C.P. copper connecting pipe , 450 mm long and nuts & washer with C.P. Brass flange complete including cutting and making good the Walls / Floors wherever required. | Each | 718
| 1.17 | Receiving, Unloading, Storing, transporting, testing & Commissioning of CP brass towel ring of size 150 mm dia with screw and rawl plug etc, including cutting and making good the Walls / Floors wherever required. | Each | 83
| 1.18 | Receiving, Unloading, Storing, transporting, testing & Commissioning of CP brass air purifier holder fixed to PVC rubber plug with C.P brass screw complete each. | Each | 32
| 1.19 | Receiving, Unloading, Storing, transporting, testing & Commissioning of CP towel rod with CP brass bracket of approved make fixed to PVC rawl plug with CP brass screws, making holes in walls & making good the same. (For Other areas Toilets of Basements ground & L-1) | Each | 2
| 1.2 | Receiving, Unloading, Storing, transporting, testing & Commissioning of C.P. brass Ablution health faucet assembly comprising hand held shower with 8 mm dia flexible tube with mounting bracket fixed on wall complete. | Each | 138
| 1.21 | Receiving, Unloading, Storing, transporting, testing & Commissioning of fully automatic "NO TOUCH" stainless steel finish hand drier suitable to operate on 220 volts, single phase 50 hz, A.C. power supply and directly plugged to power point complete. complete. | Each | 32
| 1.22 | Receiving, Unloading, Storing, transporting, testing & Commissioning of Grab Bar swing wall mount type for handicaped toilet including all accessories, cp screws etc. complete in all respect. | Each | 12
| 1.23 | Receiving, Unloading, Storing, transporting, testing & Commissioning of Grab Bar for handicaped toilet including all accessories, cp screws etc. complete in all respect. | Each | 12
| 1.24 | Receiving, Unloading, Storing, transporting, testing & Commissioning of Paper towel dispenser of approved model & make complete in all respects. | Each | 32
Sub of Total subhead above CO to Summary
| 2 | INTERNAL DRAINAGE (Soil, Waste, Vent, Rain water Pipe & Fittings):
| 2.01 | Providing, fixing, jointing and testing in position of ISI marked UV stabilized UPVC pipes for soil, waste Type-B as per IS : 13592 suitable for rubber ring joints for vertical pipes and solvent cement joints for horizontal pipes, including all neccessary specials and fittings (confirming to IS:14735) i.e. bends, tees, junctions (with or without doors), reducers, couplers, cowels, clamps, hangers, rubber rings etc. fixing at wall / ceiling / floor level supported by clamp & hangers etc. inside duct / suspended from floor under false ceiling for proper completion of the work. All hangers, clamps, brackets etc. shall be of galvanized iron unless specified otherwire and then supply of the same shall also be included for rates under this head. All structural supports, Hangers, clamps etc. shall be inclusive with piping and shall be ETA Approved. The rubber ring shall conform to IS:5382. All Supports shall be of GI (For Soil, Waste, AHU drain, condensate dain & Vent Pipes Horizontal and Vertical in Shafts)
| a) | 50 mm dia | RM | 60
| b) | 75 mm dia | RM | 100
| c) | 100 mm dia | RM | 2455
| d) | 150 mm dia | RM | 0
| e) | 200 mm dia | RM | 0
| 2.02 | Providing, fixing & testing uPVC pipes, conforming to IS 4985 class III (6 kg/cm2) including injection moulded fittings, jointing with solvent cement, cutting, complete with supports, hangers, clamps etc. and making good the floors and walls and jointing to trap/waste pipe and branch vent, complete of outer dia. All hangers, clamps, brackets etc. shall be of galvanized iron unless specified otherwire and then supply of the same shall also be included for rates under this head. All structural supports, Hangers, clamps etc. shall be inclusive with piping and shall be ETA Approved.- For indirect waste inside toilets/kitchen
| a) | 32 mm OD | RM | 280
Indirect waste | b) | 40 mm OD | RM | 120
| c) | 50 mm OD | RM | 120
| 2.03 | Providing & fixing UPVC soil, waste, vent pipework comprising uPVC pipe conforming to IS :4985-1983 class-III or as specified below and fittings (moulded as well as fabricated) like elbows, bends, reducers, threaded tail pieces, caps, suitable elbow with suitable extension piece for drain point and other specials. jointing with cement solvent, chasing, cutting and making good the walls & floors pipes laid in floors shall be encased with 40 mm thick concrete all around, complete in all respects including testing of complete installation. (Rain Water pipes)
| a) | 110 mm dia | RM | 35
| b) | 160 mm dia | RM | 495
| c) | 200 mm dia | RM | 0
| 2.04 | Providing and fixing UPVC P-Trap of self cleansing design having 50mm water seal with screwed down or hinged grating with or without vent arm complete, including cost of cutting all supports, clamps, hangers and making good the walls and floors:
| a) | 110 mm inlet & 110 mm outlet | Each | 225
| b) | 110 mm inlet & 75 mm outlet | Each
FT/UT
| 2.05 | Providing, fixing, testing and commissioning of uPVC Ceiling cleanout plug conforming to IS:14735 – 1999 complete with all fitting, accessories and civil works.
| a) | 100 mm dia. | Each | 104
| b) | 150 mm dia. | Each | 0
| c) | 200 mm dia. | Each | 0
| d) | 250 mm dia. | Each
| 2.06 | Providing, fixing and testing of uPVC SWR inlet fittings with two or three saddle inlets of 40, 50 or 63 mm size, fabricated from 110 mm outer dia uPVC pipes and fixed to uPVC traps with solvent cement joint complete in all respect. | Each | 225
INLET FITTING | 2.07 | Providing & fixing UPVC Floor Drain 110x50mm dia including cutting and shaping to required size for floor drain.
| a) | 110x50mm OD | Each | 68
FD
| 2.08 | Providing & fixing 1 mm thick stainless steel grating with cockroach trap rim of approved design including setting in floor with cement mortar. (For Trap and Floor Drain)
| a) | 100 mm dia for FD (Make: Camry, Model: CCR-S-102) | Each | 68
GRATING | b) | 150 mm dia for FT (Make: Camry, Model: CCR-WFSST-150) | Each | 225
| 2.09 | Providing, fixing to the inlet mouth of rain water pipe CI grating /Jali of following size including all fitting and accessories including civil work. (For Balcony Drainage)
|  | 100 mm x 100 mm size (Make: Neco/Neer/GMGR) | Each | 0
| 2.1 | Providing and fixing straight/offset type Macfit single body push fit type WC Pan Connector with factory supplied spring loaded seal guard with integrated single mould sealing fins made of flexible EVA Body, including bush/adaptor for use with CI Pipe as supplied with Pan Connector (For European water closet) [Make : McAlpine] | Set | 138
WC CONNECTOR | 2.11 | Providing, fixing and testing and commissioning of GI pipes Class 'B' (Medium duty, yeild strength min 195N/mm2) of approved make conforming to IS 1239-1982 complete with G.I. fittings such as tees, crosses, plugs, sockets, elbows, reducers, unions, sleeve pieces, check nuts etc including jointing with C.I. pipes (wherever required), cutting & making good the walls, floors, R.C.C. work etc. including all hangers, supports, clamps, cutting chases & filling the same, painting the GI pipes with two coats of bitumastic paint, wrapping with one layer of polythene tape. 400 micron thick and applying a final coat of bittumestic paint complete including surface preparation. All hangers, clamps, brackets etc. shall be of galvanized iron unless specified otherwire and then supply of the same shall also be included for rates under this head. All structural supports, Hangers, clamps etc. shall be inclusive with piping and shall be ETA Approved. (for Sump riser, STP Bye pass, basement floor drain).
| a) | 80 mm dia | RM | 220
SUMP RISER | b) | 100 mm dia | RM | 25
| b) | 150 mm dia | RM | RO
| 2.12 | Providing, fixing to the Scupper/L shape drain with bottom/side outlet for rain water pipe inc. grating / Jali of req. size including all fitting and accessories including civil work.
| a) | 150 mm Outlet | Each | 81
| 2.13 | Providing & fixing rain water `Khurras' of following size with required depth with lead flashing around the pipe with one piece lead sheet of 3 mm thick set on a layer of cold bitumen. Including Heavy duty CI grating as per drawing complete as required.
| a) | 450mm x 450mm | Each | 81
Sub of Total subhead above CO to Summary
| 3 | DOMESTIC/ FLUSHING WATER SUPPLY (Internal)
| 3.01 | Providing and fixing chlorinated polyvinly chloride (CPVC) CTS SDR 11 hot & cold water pipes conforming to IS capable to withstand 27.6 kg/cm² at room tempreature water and 7.03 kg/cm² at 82°C and all fittings of CPVC SDR 11 like elbow, tee, reducers, couplers, brass threated male & female (adapoters, elbow, tees). The pipe fitting joining to be done with solvent cement as per manufacturers specifications & recommendations. The above includes chaise cutting with double blade chaze cutter (no chisel/hammer allowed to use) fixing supporting the pipes & fittings, at wall/ceiling level supported by galvanized clamps, hangers etc, as per specification of pipes fittings testing of assembley. Chased area has to be packed with GI Rhombus mesh of 200mm width and shall be pasted with 1:2 mortar.
Fixing/supporting the pipes & fittings at wall/ceiling level supported by galvanized clamps, hangers etc, as per specification. All hangers, clamps, brackets etc. shall be of galvanized iron unless specified otherwire and then supply of the same shall also be included for rates under this head. All structural supports, Hangers, clamps etc. shall be inclusive with piping and shall be ETA Approved. GI pipe sleeves suitable higher size shall be provided wherever the pipes are crossing the fire rated walls / floors slab and sealing the sleeves with glass wool in between and fire sealant compound at either end all as per Project Manager's / Consultant requirement. All termination points for installation of faucets shall have brass termination fittings. Installation shall be to as per Technical Manual of manufacturer of pipes & fittings.(Cost including maximum of 7.5x7.5cm chasing in wall and floors for the pipe and making good the same.)(Concealed or exposed internal within toilet after ball valve) - Domestic & Flushing water supply.
The Pipes and fittings shall be capable of withstanding 15 Bar pressure at 25 Deg C. The Testing pressure shall be 1.5 times the working pressure of the pipe
| a) | 15mm OD | RM | 830
| b) | 20mm OD | RM | 1970
| c) | 25mm OD | RM | 380
| d) | 32mm OD | RM | 240
| e) | 40mm OD | RM | 100
| f) | 50mm OD | RM | 70
| 3.02 | Providing, fixing, jointing and testing in position flowguard cPVC sch 40 pipes with sch 80 fittings, UV stabilized, confirming to ASTM D 1785 & ASTM D 2467 suitable for cold water supply in concealed or exposed works complete with all necessary fittings i.e. elbows, tees, bends, couplers, reducers, unions, plugs, transition fittings, clamps including jointing the pipe and fitings by solvent cement over primer coat as per ASTM D 2564 including proper support and clamped complete as required included threaded fittings with or without brass inserts as required by the Engg-in-charge for proper completion of the work. All termination points for installation of faucets shall have brass terminal fittings. (The price excludes cutting chases and making good the walls) (For Supply risers and downtakes in shaft)
| a) | 20 mm Nominal Size / 26.67 mm OD (min. wall tk - 2.87 mm) | Mtr. | 20
| b) | 25 mm Nominal Size / 33.40 mm OD (min. wall tk - 3.38 mm) | Mtr. | 30
| c) | 32 mm Nominal Size / 42.16 mm OD (min. wall tk - 3.56 mm) | Mtr. | 30
| d) | 40 mm Nominal Size / 48.26 mm OD (min. wall tk -3.68 mm) | Mtr. | 60
| e) | 50 mm Nominal Size / 60.32 mm OD (min. wall tk - 3.91 mm) | Mtr. | 140
| f) | 65 mm Nominal Size / 73.02 mm OD (min wall tk - 5.16 mm) | Mtr. | 50
| g) | 80 mm Nominal Size / 73.02 mm OD (min wall tk - 5.16 mm) | Mtr. | 0
| h) | 100 mm Nominal Size / 73.02 mm OD (min wall tk - 5.16 mm) | Mtr. | 0
| i) | 150 mm Nominal Size / 73.02 mm OD (min wall tk - 5.16 mm) | Mtr. | 0
| 3.03 | Supplying, fixing, jointing and testing in position the following heavy class (Class C) GI pipes conforming to IS:1239 cut to required lengths including all necessary fittings (All fittings shall confirm to IS:1879 - part 1 to 10) and specials such as bends, tees, unions, reducers, flanges & plugs etc. Fixing at wall/ceiling/floor level supported by galvanized clamps, hangers, M.S structural support,brick pedestals etc as per specification or chasing in wall / floor and making good the same by using 1:1 cement mortar over the wire mesh. All hangers, clamps, brackets etc. shall be of galvanized iron unless specified otherwire and then supply of the same shall also be included for rates under this head. All structural supports, Hangers, clamps etc. shall be inclusive with piping and shall be ETA Approved. Threading, jointing, and making proper connections. Cutting hole in wall / floor / slab and making good the same.Cost shall be inclusive of providing two coats of synthetic enamel paint of approved shade on exposed pipes, over a coat of zinc, primer, including two coats of synthetic enamel painting of legends with direction arounds. All Supports shall be of GI (For Terrace & OHT Piping.)
| a) | 50mm dia | Mtr. | 50
| b) | 65mm dia | Mtr. | 100
| c) | 80mm dia | Mtr. | 30
| d) | 100mm dia | Mtr. | RO
| e) | 150mm dia | Mtr. | RO
| 3.04 | Providing & fixing thermal insulation on water supply pipes a flexible elastomeric foam of closed cells structure having thermal conductivity of 0.038 W/M.K at 40o C, water vapour permeability fire propagation including all accessories complete as per specification. All joints shall be sealed with adhesive & cotton tape, shall be applied to give uniform appearance & finished with polished protective coating.(For Vertical/Exposed pipes).
|  | 15 mm [6mm thick insulation] | Mtr. | 0
|  | 20 mm [6mm thick insulation] | Mtr. | 0
|  | 25 mm [6mm thick insulation] | Mtr. | 0
|  | 32 mm [9mm thick insulation] | Mtr. | 0
|  | 40 mm [9mm thick insulation] | Mtr. | 0
|  | 50 mm [9mm thick insulation] | Mtr. | 0
|  | 65 mm [13mm thick insulation] | Mtr. | 0
|  | 80 mm [13mm thick insulation] | Mtr. | 0
|  | 100 mm [13mm thick insulation] | Mtr. | 0
| 3.05 | Supply, Installation, Testing & Commisioning of Mechanical Protection with 7 ml Glass cloth & UV protective coating (Insulation not to be part of this item as the same is measured separately) on the above insulated piping with Alkali resistance glass fiber fabric (Paramount Polytreat Chemicals Make Parafeb-GFC / Approved Equal) of 5 to 7 mil (minimum) thickness reinforcement and Starbond 30-36 / equal coating. Nominal diameter of Pipes and insulation thickness in mm as indicated below: (Exposed work on terrace / ducts)
|  | For 65 mm | Mtr. | 0
|  | For 80 mm | Mtr. | 0
|  | For 100 mm | Mtr. | 0
| 3.06 | Providing & fixing Full Way Lever operated Ball Valve with threaded / flanged joints complete with nuts, bolts, gaskets, washers etc.
MOC: Forged Brass, Nickel Plated, Full Bore
Ball: Forged brass Hard Chrome Plated mirror smooth finish with PTFE Seat
Handle: Dacromat rugged steel with PVC grip
Lever and Nut: Nyloc self-locking type
Stem Seals to be Double “O” Rings of H-NBR (Hydro Generated Nitrile Rubber)
Pressure Rating: PN16
| a) | 15 mm dia | Each | 14
| b) | 20 mm dia | Each | 36
| c) | 25 mm dia | Each | 10
| d) | 32 mm dia | Each | 20
| e) | 40 mm dia | Each | 26
| f) | 50 mm dia | Each | 13
| 3.07 | Pressure Reducing Valve Station
Providing & Fixing of Pressure Reducing Valve Station with following details and in the following sequence:
Pressure gauges and isolation valves before and after PRV, with Bypass line (without PRV) with isolation valve in by pass line and necessary arrangement , mating flanges to suit the specified piping material,as specified and complete as required in water supply pipes. on-line type as shown in drawings/schematics and in accordance with technical specification. To suit pressure rating as specified on schematics and specification.For inlet and outlet pressure rating refer schematics and drawings.
Main Line Inlet:
Ball Valve
Y-Strainer
Pressure Gauge
PRV Main Branch:
Ball Valve
PRV
Ball Valve
Bypass Branch:
Ball Valve
Main Line Inlet:
Pressure Gauge
Specifications of above items shall be:
Ball Valve:
MOC: Forged Brass, Nickel Plated, Full Bore
Ball: Forged brass Hard Chrome Plated mirror smooth finish with PTFE Seat
Handle: Dacromat rugged steel with PVC grip
Lever and Nut: Nyloc self-locking type
Stem Seals to be Double “O” Rings of H-NBR (Hydro Generated Nitrile Rubber)
Pressure Rating: PN16
Y-Strainer:
Screwed/flanged with stainless steel fine wire mesh perforated sheet basket with necessary flange/ unions nuts, bolts and washers complete as required
Body: Cast Iron
Filter: SS
Pressure Rating: PN16
Pressure Gauge:
Burden type Stainless Steel dial type pressure gauge with brass isolation valve and pipe
Dial Diameter : 100 mm
Caliberation : 0-10 Kg/cm2
PRV:
Material of Construction:
Body: Forged brass nickel plated with brass diaphragm
Seal: Stainless Steel
O-Ring: NBR Nitrile Elastomeric Diaphragm
DZR Brass Rod
End: Screwed BSP female
Pressure Rating: PN16
Pressure Range: 10 Bar down to 1.5 Bar (adjustable)
| a) | 25 mm dia | Each | RO
| b) | 32 mm dia | Each | RO
| c) | 40 mm dia | Each | 2
| d) | 50 mm dia | Each | 1
| e) | 65 mm dia | Each | 3
| f) | 80 mm dia | Each | 2
| g) | 100 mm dia | Each | RO
| 3.08 | Pressure Reducing Valves (SPARE)
Providing of Spare Pressure Reducing Valves confirming specifications as descibed in item no. 3.04.
| a) | 25 mm dia | Each | RO
| b) | 32 mm dia | Each | RO
| c) | 40 mm dia | Each | 1
| d) | 50 mm dia | Each | 1
| e) | 65 mm dia | Each | 1
| f) | 80 mm dia | Each | 1
| g) | 100 mm dia | Each | RO
| 3.09 | Providing and fixing air vent valve as per EN 29000 – ISO9000 including all fitting & accessories.
MOC:
Body: Forged Brass
Seal: EPDM
Float: PP
Spring: Stainless Steel
Pressure Rating: PN10
| a) | 15 mm dia | Each | 5
| 3.1 | Providing & fixing Butterfly valve complying to IS: 13095 and AWWA Standard (upto 150mm dia with hand lever operation & above with gear box operation) including rubber gasket, flanges, nuts, bolts, washers & painting complete as required.
Material of Construction:
Body: Graded Cast Iron duly powder coated
Disc: Ductile Iron Electro less Nickel plated having mirror smooth edges
Shaft: SS Single piece through shaft Spline design technology
Replaceable EPDM rubber sleeve with hard backing
Pressure Rating: PN16
| a) | 65 mm dia | Each | 3
| b) | 80 mm dia | Each | 0
| b) | 100 mm dia | Each | 1
| b) | 150 mm dia | Each | 0
| 3.11 | Disinfecting water mains by Domestic & Flushing with water containing Bleaching Powder at 0.5 gm per liter of water and cleaning the same with fresh water, operation to be repeated three times including getting the samples of water from disinfected main tested in the municipal laboratory. | LS | 1
Providing and fixing approved make & suitable model of R.O. plant (fully automatic operation) 1500 ltrs. Per hour flow rate having capacity to treat the raw water and average recovery not less than 35% . The operating voltage to 230 volt AC +/- 10% along with required capacity on line SS pump of approved make (3HP minimum) and solenoid valves, dry run protection of pump, automatic tank level control, inbuilt auto flush timer for periodic flushing of membranes, storage tank (3.0 mm (minimum) thick S.S. 304 sheet) 2500 lts 2 Nos. of suitable size and ita supporting structure, over voltage and over current protection with switch mode power supply system complete in all respects including installation and fittings with the following provisions:
10 micron polypropylene sediment pre filter
10 micron bacteriostatic activated carbon block on line micron filter with 5 micron rating
Required Nos. and size of reverse osmosis memberane with 0.0001 micron pore size energy saving poly amide type
UV lamp of minimum capacity 1500LPH and minimum lamp wattage 15W
|  | MS powder coated frame efficient of TDS removal more than 90%. Antiscalant dosing and acid dosing system for self flushing/cleaning.Pressure switches and gauges, pH correction dosing system, Digital TDS meter, Digital pH meter, electric panel and necessary instrumentation included Rotameter.MS structure and fibre glass sheet weather protection cover as per site condition. | Set | 1
| 3.12 | Providing and fixing of Chiller for RO water of given capacity with required tank capacity including structure of machine compressor with overheating protection over current protection flow switch protection and exhaust overheating protection complete in all respect.
|  | 250 LPH (1w+1s) | Nos. | 2
Sub of Total subhead above CO to Summary
| 4 | EXTERNAL WATER SUPPLY SYSTEM
| 4.01 | Excavating trenches of required width for pipes, cables, etc including excavation for sockets also including for cement concrete cradles, and dressing of sides, ramming of bottoms, depth up to 1.5m including getting out the excavated soil, and then returning the soil as required, in layers not exceeding 20 cm in depth including consolidating each deposited layer with minimum 95% by ramming, watering etc. and disposing off surplus excavated soil as directed, within a lead of 50 m.
| a) | Pipes, cables etc. exceeding 80 mm dia but not exceeding 300mm OD. | RM | 50
| 4.02 | Providing and laying S & S Ductile Iron Pipes (Class K-9) conforming to IS: 8329 suitable for push on flexible rubber (Tyton) joints, lowering the pipe in trenches to required depth and alignment including the cost of connecting fittings for D.I Pipe to G.I.Pipe and making joints complete in all respects. Cost shall be inclusive of providing protection to pipe all round / haunches - External water supply - municipal, tanker
| a) | 80 mm dia | RM | 50
| b) | 100 mm dia | RM | RO
| 4.03 | Providing & fixing Butterfly valve complying to IS: 13095 and AWWA Standard (upto 150mm dia with hand lever operation & above with gear box operation) including rubber gasket, flanges, nuts, bolts, washers & painting complete as required.
Material of Construction:
Body: Graded Cast Iron duly powder coated
Disc: Ductile Iron Electro less Nickel plated having mirror smooth edges
Shaft: SS Single piece through shaft Spline design technology
Replaceable EPDM rubber sleeve with hard backing
Pressure Rating: PN16
| a) | 80 mm dia | Each | 1
| a) | 100 mm dia | Each | RO
| 4.04 | Providing & fixing Dual Plate Check valve (NRV) including rubber gasket, flanges, union, nuts, bolts, washers & painting complete as required.
Material of Construction:
Body: Cast Iron Powder Coated
Seat Ring: EPDM
Disc: Ductile Iron Electro less Nickel plated/SS (304)
Spring & Hinge Pin: SS 304 (CF 8)
Stem: SS 410
Washers: P.T.F.E
Pressure Rating: PN16
| a) | 80 mm dia | Each | 1
| 4.05 | Providing, Installtion, testing and commissioning of Bronze ferrule connection with all accessories I.e. union, nipple, elbow, end point cap and reducing elbow and connecting with (main WS pipe) CILA/GI pipe by drilling and tapping including cost of ferrule complete in all respects. | Each | 0
| 4.06 | Constructing brick masonry chamber (for housing valves, meters etc.) with 75 class designation brick work in cement mortar 1:5 (1 cement :5 fine sand) for valves cement conc. top slab 1:2:4 (1 cement :2 coarse sand :4 graded stone aggregate 20 mm nominal size) necessary excavation, foundation conc. 1:5:10 (1 cement :5 fine sand :10 graded stone aggregate 40 mm nominal size) & inside plastering with cement mortar 1:3 (1 cement :3 coarse sand) 12 mm thick finished with a floating coat of neat cement complete as per standard design:
| a) | 300x300x600 mm size (inside) chamber with Double Seal DI Heavy Duty cover (lockable) size 250x250 mm (inside) with DI frame fixed in cement conc. Slab. | Each | RO
| b) | 450x450x750 mm size (inside) chamber with Double Seal DI Heavy Duty lockable 300 x 300 mm (inside) with D.I. frame fixed in cement conc. slab. | Each | RO
| c) | 600x600x900 mm size chamber with Double Seal DI Heavy Duty cover (lockable) size 300x300 mm inside with D.I. frame fixed in cement conc. slab. | Each | 1
Sub of Total subhead above CO to Summary
| 5 | GARDEN HYDRANT SYSTEM
| 5.01 | Providing & laying UPVC pressure pipes of 8Kg/Sq.cm pressure rating Class- IV (IS : 4985-2000) including fittings, tees, bends, clamps, coupling and adaptors supports, and jointing with solvent joint, testing and necessary earth work in excavation, backfilling, disposal of surplus earth with a lead up to 100m complete, compaction and consolidation Including sand bedding all around UPVC pipe & fittings and thrust blocks at bends as per standard design (For garden hydrants).
| a) | 25 OD | RM | 70
| b) | 40 OD | RM | 340
| c) | 50 OD | RM | 80
| d) | 63 OD | RM | 40
| 5.02 | Providing and fixing forged brass body quarter turn lever operated ball valve with forged brass hard chrome plated ball, disc & gland packing shall be PTEF tested to 16 Kg/Sq.cm pressure including GI nipple and threaded hose receiver complete as required.
| a) | 20 mm nominal bore | Each | 14
| b) | 25 mm nominal bore | Each | RO
| 5.03 | Construction brick masonry chamber (for Housing Lawn hydrant) Garden Hydrant with 75 class designation brick work in cement mortar 1:5 (1 cement : 5 find sand) for valve, DI Heavy Duty cover with frame fixed in cement concrete slab 1:2:4 mix (1 cement : 2 coarse sand : 4 graded stone aggregate 20mm nominal size) necessary excavation foundation concrete 1:5:10 (1 cement : 5 fine sand : 10 graded stone aggregate 40mm nominal size) and inside plastering with cement mortar 1:3 (1 cement : 3 coarse sand) 12 mm thick finished with a floating coat of neat cement complete as per standard design.
| a) | 300x300x600 mm size (inside) chamber with Double Seal DI Heavy Duty cover (lockable) size 250x250 mm (inside) with DI frame fixed in cement conc. Slab. | Each | 14
| b) | 600x600x750 mm size chamber with Double Seal DI Heavy Duty cover (lockable) size 300x300 mm inside with D.I. frame fixed in cement conc. slab. | Each | RO
| 5.04 | Butterfly Valve :
Providing and fixing wafer end type cast iron butterfly valves conforming to IS : 13095 & BS : 5155 tested to 16 kg/sq.cm pressure (including flanges) (for GH Ring).
| a) | 50 mm dia | Each | 1
Sub of Total subhead above CO to Summary
| 6 | EXTERNAL SEWERAGE & DRAINAGE SYSTEM
| 6.01 | Earth Work in Excavation of required width for storm water drainage pipes including excavation for sockets and dressing of sides, ramming of bottom depth up to 1.5 m including getting out the excavated soil and then returning the soil as required in layer not exceeding 20 cms in depth including consolidating each deposited layers by ramming, watering etc. and disposing of surplus excavated soil as directed within a lead of 50 m for all kinds of soil.
| a) | Pipes, exceeding 80 mm dia but not exceeding 300 mm dia. | RM | 730
| b) | Pipes, exceeding 300 mm dia but not exceeding 600 mm dia. | RM | 50
| 6.02 | Extra for excavating trenches for pipes, cables etc in all kinds of soil for depth exceeding 1.5m, but not exceeding 3m. (Rate is over corresponding basic item for depth up to 1.5 metre)
| a) | Pipes, exceeding 80 mm dia but not exceeding 300 mm dia. | RM | RO
| b) | Pipes, exceeding 300 mm dia but not exceeding 600 mm dia. | RM | RO
| 6.03 | Providing,lowering,laying,fixing in position and jointing of DWC HDPE Rat Propellant Pies at all levels / depth of Class SN 4,Structured Wall Polyethylene Systems for non pressure underground sewerage & dranage applicationby non smooth external surface,IS 16098 (Part 2) Type B marked in complete including all material labour, testing and commisioning as per technical specifications, drawings and as per direction of engineer(E/W to be measured separately)including all local and other taxes, transportation, freight charges, loading/ unloading, conveyance of the department store, etc (OD dia).The works include cost of close timbering beyond 1.50 mtr average invert depths,shoring & shuttering as per standard specification complete in all respects,as per direction of engineer in charge for following average invert depths and class of pipe.
| a) | 150 mm dia | RM | 100
| b) | 200 mm dia | RM | 20
| c) | 250 mm dia | RM | 200
| d) | 300 mm dia | RM | 360
| e) | 400 mm dia | RM | 50
| f) | 500 mm dia | RM
| 6.04 | Providing and laying 150 mm thick cement concrete 1:5:10 mix ( 1 cement : 5 coarse Sand : 10 graded stone aggregate 40 mm nominal size) upto haunches including bed concrete 150 mm as per standard design.
| a) | 200 mm dia | RM | 20
| b) | 250 mm dia | RM | 200
| c) | 300 mm dia | RM | 360
| d) | 400 mm dia | RM | 50
| e) | 500 mm dia | RM | 0
| 6.05 | Providing and laying cement concrete 1:5:10 (1 cement : 5 coarse sand : 10 graded stone aggregate 40 mm nominal size) all-round over pipes including bed concrete as per standard design (Bed thickness 150mm & Alround thickness 100mm).
| a) | 150 mm dia | RM | 100
| 6.06 | Providing and fixing square mouth (S.W) gully trap grade `A' complete with C.I. grating brick masonry chamber with bricks of class designation 75 and water tight double seal C.I. cover with frame of 300 x 300 mm internal size. The weight of cover to be not less than 4.5 kg and frame to be not less than 2.70 kg. as per standard design.
| a) | 100 x 100 mm size ‘P’ type. | Each | 0
| b) | 150 x 150 mm size 'P' type | Each | 4
| 6.07 | Catch Basin Chamber for Storm Water:
Constructing brick masonry road gully chamber unit brick of class designated 75 in cement mortar 1:4 (1 cement :4 coarse sand) including 500 x 450 mm precast DI Heavy Duty horizontal grating with frame complete as per standard design.
| a) | Size 50 x 45 x 60 cm Depth up to 750mm | Each | 50
| b) | Size 60 x 60 x 60 cm Depth up to 900mm | Each | RO
| 6.08 | Constructing water tight brick masonry manhole with 75 class designation bricks in cement mortar 1:6 (1 cement :6 coarse sand), R.C.C. top slab with 1:2:4 mix (1 cement :2 coarse sand :4 graded stone aggregate 20 mm nominal size). Foundation concrete 150 mm thick 1:4:8 mix (1 cement :4 coarse sand :8 graded stone aggregate 40 mm nominal size), inside and outside plastering 12 mm thick with cement plaster 1:3 (1 cement :3 coarse sand) finished with a floating coat of neat cement and making channels and benching in cement concrete 1:2:4 mix (1 cement : 2 coarse sand : 4 graded stone aggregate 20 mm nominal size) finished with a floating coat of neat cement complete as per standard design, plastic coated M.S 20 mm square bar foot rests including fixing in 20 x 20 x 10 cm cement conc. blocks neatly finished, complete with Double Seal DI cover Heavy duty of adequate size as per standard design and approved drawings. (Price shall include the, cost of excavation, back filling, disposal of surplus earth, foot rests dewatering & water proofing of manholes as directed at site & other associated civil works).
| a) | Inside size 600mm x 600 mm Depth up to 600mm | Each | 2
| b) | Inside size 750mm x 750 mm Depth up to 800mm | Each | RO
| c) | Inside size 800mm x 900 mm Depth up to 1000mm | Each | RO
| 6.09 | Constructing brick masonry circular type manhole 0.91 m internal dia at bottom and 0.56m dia at top in cement mortar 1:4 (1 cement : 4 coarse sand), in side cement plaster 12 mm thick with cement mortar 1:3 (1 cement : 3 coarse sand) finished with a floating coat of neat cement, foundation concrete 1:3:6 mix (1 cement : 3 coarse sand : 6 graded stone aggregate 40 mm nominal size), and making necessary channel in cement concrete 1:2:4 (1 cement : 2 coarse sand : 4 graded stone aggregate 20 mm nominal size) finished with a floating coat of neat cement all complete as per standard design.
0.91 m deep with double seal DI perforated cover and frame (heavy duty HD-20 grade designation) 560 mm internal diameter conforming to IS 12592, total weight of cover and frame to be not less than 182 Kg., fixed in cement concrete 1:2:4 (1 cement : 2 Coarse sand : 4 graded stone aggregate 20 mm nominal size) including centering shuttering all complete. (foot rests shall be paid for separately).
|  | With F.P.S. bricks class designation 75. | Each | 35
NOTE:DI MAIN HOLE COVER TO BE TAKEN
| 6.1 | Extra depth for circular type manhole 0.91m Internal dia (at bottom) with beyond 0.91 m to 1.67m. | RM | 2
| 6.11 | Constructing brick masonry circular manhole 1.22 m internal dia at bottom and 0.56m dia at top in cement mortar 1:4 (1 cement : 4 coarse sand), in side cement plaster 12 mm thick with cement mortar 1:3 (1 cement : 3 coarse sand) finished with a floating coat of neat cement, foundation concrete 1:3:6 mix (1 cement : 3 coarse sand : 6 graded stone aggregate 40 mm nominal size), and making necessary channel in cement concrete 1:2:4 (1 cement : 2 coarse sand : 4 graded stone aggregate 20 mm nominal size) finished with a floating coat of neat cement all complete as per standard design.
1.68 m deep with Double Seal DI perforated cover and frame (heavy duty HD-20 grade designation) 560 mm internal diameter conforming to I.S. 12592, total weight of cover and frame to be not less than 182 kg fixed in cement concrete 1:2:4 (1 cement : 2 coarse sand : 4 graded stone aggregate 20 mm nominal size) including centering shuttering all complete. (foot rests shall be paid for separately).
|  | With F.P.S. bricks class designation 75. | Each | 5
| 6.12 | Extra depth for circular type manhole 1.22 m internal dia (at bottom) beyond 1.6 pm to 2.29m. | RM | 2
| 6.13 | Rain Water Harvesting system :
Construction of rain water harvesting size 4.5 x 2.0 x 3.0m effective depth for the re-charging of storm water run off including the civil work with following specification given below (or structural requirement with local site condition) and as per attached drawings complete in all respects: -
| i) | De-Silting cum Oil and Grease Separator Chamber:
Providing and constructing masonry de-silting chamber 2000mm x 1200mm with 1500mm depth inside with 75 class designated brick work in cement mortar 1:6 (1cement : 6 fine sand) with DI double seal Heavy duty 560mm dia manhole cover (2Nos.). top slab 1:2:4 mix (1cement : 2coarse sand : 4 graded stone aggregate 20mm nominal size) with minimum 1.5% reinforcement, foundation concrete 1:5:10 (1cement : 5 fine sand:10 grade stone aggregate 20mm nominal size including baffle wall, necessary excavation, back filling and disposal of surface earth. Complete with inlet, outlet and overflow arrangement. Foot rest @400mm c/c, grating of required size with 16mm sq.bars and frame @20mm clear spacing fixed at month of pipe as per site conditions and direction of Engineer in charge.
| ii) | Drilling: (Double Bore)
Drilling percolation borehole 300mm dia with reverse rotary method in all types of soil up to 30 m (approx.) depth including cost for mobilization of rig and making good the area upon completion of work. Contractor shall arrange for all necessary tools, water and consumable and laying for drilling.
| iii) | Providing and laying pea gravel all around the casing pipe.
| iv) | 160 mm dia slotted UPVC pipe of 6 Kg/cm2 - 25 m - 30m or as per site sub-strata or set as per direction of Engineer- in charge
| v) | 160 mm dia UPVC blind pipe of 6 Kg/cm2 with bail plug and well cap, complete as per approved drawing.
| vi) | Rain Water Harvesting Pit Filtration Chamber:
Providing and constructing rain water harvesting well/filtration chamber of size 3.5 x 4.5 m effective depth or as per approved drawings inside with 75 class designated brick work in cement motor 1:6 (1cement : 6 fine sand) with top slab 1:2:4 mix (1cement : 2 course sand :4 graded stone aggregate 20mm nominal size) with minimum 1.5% reinforcement , foundation concrete 1:5:10 (1cement : 5 fine sand and 10 graded stone) aggregate 20mm nominal size including 300mm depth Boulder 10-20mm, 300mm depth gravel 5-10mm size, 300mm depth coarse sand 1.5-2.0mm size including necessary excavation, back filling and disposal of surface earth complete with inlet, outlet, overflow arrangement pvc coated Foot Rest, 100mm dia deep holes @500mm c/c to be provided 1200 c/c above the bottom of wall, 100mm C.I vent pipe -2m height with cowls.
|  | Rate shall include excavation, back filling and all other operations necessary for completing the job. | Job | 7
| 6.14 | Making connection of sewer /storm water line with external manhole including breaking into and making good the walls, floors with cement concrete 1:2:4 mix (1 cement :2 coarse sand : 4 graded stone aggregate 20 mm nominal size) cement plastered on both sides with cement mortar 1:3 (1cement: 3 Coarse sand) finished with a floating coat of neat cement and making necessary channels for the drain etc. complete. | Each | 1
| 6.15 | Providing orange colour safety foot rest of minimum 6mm thick food grade plastic encapsulated as per IS : 10910 on 12mm dia steel bar conforming to IS : 1786 having minimum crosssection as 23 mm x 25mm and over all minimum length 263mm and width as 165mm with minimum 112mm space between protruded legs having 2 mm tread on top surface by ribbing or chequering besides necessary and adequate anchoring projections on tail length on 138 mm as per standard drawing and suitable to with stand the bend test and chemical resistance test as per specifications and having manufacturer's permanent identification mark to be visible even after fixing, including fixing in manholes with 30x20x15 cm cement concrete block 1:3:6 (1 cement : 3 coarse sand : 6 graded stone aggregate 20 mm nominal size ) complete as per design. | No. | 420
Sub of Total subhead above CO to Summary
| 7 | MISCELLANEOUS ITEMS
| 7.01 | Providing and fixing G.I. puddle flange comprising of 600 mm dia long G.I. class 'C' pipe (screwed end up to 50 mm & flange for more than 50 mm dia) with 6 mm thick M.S plates of required size including cutting holes in centre of plate, inserting pipe & making welded (Arc) joint complete. Same shall be installed with TEC welded joint in position with reinforcement bars of RCC tank wall/slab including making cutout in shuttering during concrete casting of tank of following diameter. (Location: underground/ overhead tanks.) (Flanges shall confirm to BS10 Table E) .
| a. | 25 mm dia (Screwed ends GI plate 6 mm thick; 100 mm x 100 mm plus dia of pipe). | No. | 14
| b. | 32 mm dia (Screwed ends GI plate 6 mm thick; 100 mm x 100 mm plus dia of pipe). | No. | 5
| c. | 40 mm dia (Screwed ends GI plate 6 mm thick; 100 mm x 100 mm plus dia of pipe). | No. | 0
| d. | 50 mm dia (Screwed ends GI plate 6 mm thick; 100 mm x 100 mm plus dia of pipe). | No. | 14
| e. | 65 mm dia (Flanged ends GI plate 6 mm thick; 100 mm x 100 mm plus dia of pipe). | No. | 0
| f. | 80 mm dia (Flanged ends GI plate 6 mm thick; 100 mm x 100 mm plus dia of pipe). | No. | 2
| g. | 100 mm dia (Flanged ends GI plate 6 mm thick; 250 mm x 200 mm plus dia of pipe). | No. | 23
| h. | 150 mm dia (Flanged ends GI plate 6 mm thick; 250 mm x 200 mm plus dia of pipe). | No. | 9
| i. | 200 mm dia (Flanged ends GI plate 6 mm thick; 250 mm x 200 mm plus dia of pipe). | No. | 2
| j. | 250 mm dia (Flanged ends GI plate 6 mm thick; 250 mm x 200 mm plus dia of pipe). | No. | 2
| k. | 300 mm dia (Flanged ends GI plate 6 mm thick; 250 mm x 200 mm plus dia of pipe). | No. | 0
| 7.02 | WATER TANK COVER
| a) | Providing and fixing 560 mm dia Double seal DI Medium duty water tank cover with lockable arrangement complete in all respects including all fitting & accessories. (Location: OH Tank) | Each | 3
| b) | Providing and fixing 560 mm dia Double seal DI Heavy duty water tank cover with lockable arrangement complete in all respects including all fitting & accessories. (Location: UGT) | Each | 12
| 7.03 | SUMP PIT COVER
| a) | Providing and fixing 560 mm dia / 600 X 600mm Double seal DI Heavy duty Manhole cover with lockable arrangement complete in all respects including all fitting & accessories. (Location: Basement sump pit, Lift Pit, Sewage Sump Pit, Pump Room sump pits.) | Each | 8
| 7.04 | G.I VENT PIPE
Providing and fixing G.I. Vent Pipe class 'B' (medium duty) for R.C.C water storage tanks comprising of 600 mm long vertical pipe, return bend with mosquito grating & cast brass perforated coupling including all associated civil work.
| a) | 100 mm dia | Each | 15
| 7.05 | UNLOADING POINT ASSEMBLY
|  | Providing and fixing unloading point assembly (for water tanker supply) consisting of 80 mm dia. G.M. instantaneous. Female inlet coupling with brass plug complete.(Truck fill point shall be housed in suitable lockable chamber). | Each | 1
| 7.06 | M.S. STRUCTURAL WORK
|  | Providing and fixing M.S. structural work fabricated from standard sections, (MS rounds, angles, channels etc.) including cutting to size, drilling, welding, including cost of fasteners, clamps in RCC structural members as directed, including two or more coats of synthetic paint over one coat of primer after surface preparation including cutting and making good walls. | Kg | 400
Sub of Total subhead above CO to Summary
| 8 | PUMPS & PUMP ROOM ACCESSORIES
Note: Contractor shall verify, calculate and submit all Pump head calculations as per site conditions before submitting Pump Technical Data Sheets
| 8.01 | Hydropneumatic Pumps
Design, Supply, Installation, Testing, & Commissioning of a pre-engineered, factory fitted, factory assembled & tested, fully integrated, highly efficient pump, skid mounted hydropneumatic system, complete comprising of :-
| i. | Vertical Inline Multistage Centrifugal Pump with Cast iron with CED coated base & head, SS-304 casing chamber and impeller and SS-316 shaft along with TEFC induction motor of 2 pole, 2900 RPM, suitable for 415±10% Volts, 3 phase, 50 Hz A.C. supply, mechanical seal, pressure transmitter, NRV, Isolation valve on delivery line. Isolation valve(PN-16), strainer at suction. The pump shall be suitable for auto/ manual operation. suction/discharge headers,skid, vibration isolators as specified in specification. The pump and motor shall in accordance with specifications. Supply, installation complete in all respects as per directions of Engineer in charge
The pump set shall be suitable for
Pump:
Pump Head - Cast Iron EN-GJ-200
Shaft- Stainless Steel 316 or Better
Impeller - Stainless Steel 304 or SS316
Outer Sleeve - Stainless Steel 304
Chamber - Stainless Steel 304
Pump Base- Cast Iron EN-GJL-250 or SS304
Coupling Guard- Stainless Steel 430
Shaft Seal- Stainless Steel 316
Neck Ring - PTFE
O-Ring for Sleeve - EPDM or FKM
Shaft Seal (Seal Face)- Silicon Carbide/SiC
Rubber Parts - EPDM or FKM
| ii. | 3-phase, fan-cooled, permanent-magnet synchronous motors, with motor efficiency is classified as IE3 in accordance with IEC 60034-30-2 should comply to the highest minimum efficiency index MEI 0.7 .The motor integrated with dedicated frequency converter in the motor terminal box. This enables continuously variable control of the motor speed, which again enables adaptation of the performance to a given requirement.
Motor:
With Floating Variable Speed Drive Mounted on Single Pump
Efficiency class - IE4/5
Totally Enclosed fan-cooled, squirrel cage permanent magnet motor
Insulation class - F
Enclosure class - IP 55
Supply Frequency - 50/60Hz ± 5%
Electrical Tolerance comly with IEC 60034
Supply voltage - 3 X 380-500V (± 10% variation)
Built in Thermistor-PTC
RPM - 2900
| iii. | A dedicated intelligent multi-pump logic controller (PLC) for control and monitoring of pumps shall be from the pump manufacturer with easy interface graphical display unit with key function. Controller should able to monitor multiple operating parameters (flow, inlet pressure, outlet pressure, cumulative flow and speed etc) to calculate best operating algorithm to pump sequence optimally. The system should be able to provide information about - operation setpoint of system, speed of individual pump, power & energy comsumption of individual pump, running hours of individual pumps, operation mode, control mode, process value and set point of the system, fault readout. Contactor overload relays and MCBs should confirm to IEC 898 – 1995/ specifications. Blinking indications for pumps start, trip, low level trip, health supply should be provided in the panel along with the ammeter & voltmeter. Control panel should also consist of a cooling fan. The PLC shall be BMS compatible and also equipped with dry run protection .
| iv. | 200 L Pressure vessel of pre-charged Carbon Steel body diaphragm tank shall be fitted to the discharge pipe with a compatible Butyl-rubber diaphragm. It shall supply water at very low flows to minimize frequent pump start and stop and water hammering. There shall be complete separation between water and air and there should be no contact between water and tank compounds to avoid corrosion. Bladders shall be suitable for sufficient elasticity to permit full expansion inside the tank to ensure better performance and longer working life. Air cell burst pressure of minimum of 5 times the vessel operating pressure and cycle tested for 2,50,000 cycles.
Note: Pump Vendor to provide Back up calculation for the same.
| v. | Pressure switches bellow type fitted with micro switch and having maximum pressure and differential scale should conform to BS-6134 standards and IP55 protection class
| vi. | Ball valves to be used should be Hot Pressed brass OT-58 with stainless steel ball and PTFE seal and O-Ring. NRVs to be used should be with Springs and O-Ring arrangement.
| vii. | Pressure Transmitter (0-10/16/25bar based on system design pressure)
| viii. | Pressure Gauge - 0-16bar
| ix. | Suction & Delivery Manifolds - Hot Dip Galvanised Iron CED coated
| x. | All cast iron parts should be CED coated.
| xi. | One NRV and isolating valve for each pump is provided on delivery side and one isolating valve is provided on suction side.
Complete set system to be mounted on a common base frame and shall follow following duty.
| a) | Irrigation Pump
Flow Rate = 90 LPM
Head = 35 M
|  | 1 Set includes 2 Pumps - 1 W+1S | Set | 1
| 8.02 | Transfer/Feed Pumps
Design, Supply, Receiving,Storing, Installation, Testing, & Commissioning of Factory fitted, factory assembled, factory tested Centrifugal Vertical Multistage Inline Pump
| i. | Pump:
Base/Housing: EN-GJL-250 or EN-GJS-500-7 Grade Cast Iron
Impeller: AISI 304 Stainless Steel
Shaft: AISI 316 Stainless Steel
| ii. | Motor:
Efficiency class - IE4/5
Vertical Totally Enclosed fan-cooled, squirrel cage permanent magnet motor
Insulation class - F
Enclosure class - IP 55
Supply Frequency - 50/60Hz ± 5%
Electrical Tolerance comly with IEC 60034
Supply voltage - 3 X 380-500V (± 10% variation)
Built in Thermistor-PTC
RPM - 2900
| iii. | General:
Pump, Motor, Coupling and Coupling guard shall be factory fitted and factory assembled at the pump manufacturer’s facility.
Sound pressure level of pumps shall be less than 73 dBA
All the pums shall be BMS compatible & with dry run protection .
| a) | Raw Water Filter feed Pump
Flow Rate = 280 LPM
Head = 35 M
|  | 1 Set includes 2 Pumps - 1 W+1S | Set | 1
| b) | Domestic Water Transfer Pump
Flow Rate = 200 LPM
Head = 65 M
|  | 1 Set includes 2 Pumps - 1 W+1S | Set | 1
| a) | Rain Water Filter feed Pump
Flow Rate = 210 LPM
Head = 35 M
|  | 1 Set includes 2 Pumps - 1 W+1S | Set | 1
| c) | Flushing Water Transfer Pump
Flow Rate = 210 LPM
Head = 65 M
|  | 1 Set includes 2 Pumps - 1 W+1S | Set | 1
| d) | Rain Water transfer Pump
Flow Rate = 90 LPM
Head = 35 M
|  | 1 Set includes 2 Pumps - 1 W+1S | Set | 1
| 8.03 | Submersible Pumps
Design, Supply, Receiving,Storing, Installation, Testing, & Commissioning of Dewatering centrifugal open impeller submersible pump with double mechanical cartridge seal including 2 nos. 65NB butterfly valve, 65NB non return valve a manifiold with an 80NB butterfly valve with all fittings accessories etc. complete.
| i. | Pump:
Impeller: Semi-open/Vortex type of Ductile Cast Iron (EN-GJS-450-10) with double Mechanical Seal having Faces. Primrary Face SIC/SIC & Secondary Cermaic/Carbon
Impeller Housing: CI (EN-GJL-200)
Pump: Cast Iron with side discharge port and double mechanical seal
All pumps shall be BMS Compatible
Pump base frame shall be SS304 or better
| ii. | Motor:
Integrated Submersible 3-Phase TEFC motor
Efficiency class - IE3
Insulation Class F (155°C)
RPM: 2900
Moisture Detector for Auto Cut-Out for Water Leakage
Temperature bi-metal sensor for motor protection in case of overheating.
| iii. | Starter cum Control Panel:
Fabricated with 14 Gauge CRCA Sheet
Voltmeter, Ammeter
Auto/Manual Selector Switch
Potential Free Contacts for BMS Connectivity
Phase Indicating Lamps
Push Buttons
TP MPCP of Suitable Rating at Incomer and Outgoings
DOL Starters
5VA CL:CTs
Necessary Wiring, Cable, Terminations, Trays, Earthing, Interlocking
Control Panel to be suitable for Operation of 2 Nos. Pumps in Auto/Manual Mode
Automatic Level Control through Float Switches and Probes
Dry Run Protection
High Level Alarm
Sequential Cyclic Timer to alternate the Pumps based on Time Interval
Dynamic LCD Display for Pump Run Status, Push Calibration and Pump Accumulative Run Time
RS485 Modbus for BMS Integration
Pump On/Trip Indication
Cable connection to motor via SS cable plug and reliable clamp connection for easy access of internals of the pump without usage of special tools.
| iv. | Sump pit Pump installation and lifting assembly
sump pit pump installation and lifting assembly suitable for 2 no. of submersible ejector pumps including ready made electro-galvanized MS lifting chain & sliding guide rail. The installation shall be complete with provision of anit-vibrator flexible connector, auto coupling union flange provision on discharge pipeline for feasibility of removing the pumps and all necessary indigenous accessories as required to complete the installation.
| v. | General:
10 m interconnecting cable to be included
The pump is ready for installation either free-standing or on an auto-coupling system.
All pumps shall be factory fabricated and factory tested. The test reports shall be submitted during the installation.
Control Panel to be in PHE Vendor Scope
| a) | Flow rate : 300 LPM
Head :25 M
Solid Handling : 8-10 MM
Location : Lower Ground
Purpose : WTP Pump Room Drainage
|  | One Set Consists of 2 Nos. Pumps (1W+1S) | Set | 1
| b) | Flow rate : 300 LPM
Head : 25 M
Solid Handling : 8-10 MM
Location : Lower Ground
Purpose : Rain Water/ Flushing Pump Room Drainage
|  | One Set Consists of 2 Nos. Pumps (1W+1S) | Set | 1
| c) | Flow rate : 200 LPM
Head : 25 M
Solid Handling : 8-10 MM
Location : Lower Ground
Purpose : Sunken Area Drainage
|  | One Set Consists of 2 Nos. Pumps (1W+1S) | Set | 4
| d) | Flow rate : 200 LPM
Head : 25 M
Solid Handling : 8-10 MM
Location : Lower Ground
Purpose : Sunken Area Drainage
|  | One Set Consists of 2 Nos. Pumps (1W+1S) | Set | 1
| e) | Flow rate : 200 LPM
Head : 25 M
Solid Handling : 35-40 MM
Location : Lower Ground
Purpose : Toilet Waste
|  | One Set Consists of 2 Nos. Pumps (1W+1S) | Set | 1
| 8.04 | Supply, Fixing, testing & commissioning of vertical MSEP filter with adequate dirt holding capacity. Fabricated from MS sheet as per manufacturer's specifications complete with intitial charge filter media including painting inside with two coats of non toxic epoxy and with one coat of zinc chromate two coats of synthetic enamel paint outside. Including concrete foudation with cement plaster complete as required. The filter shall also be provided with set of internals for raw water inlet and bottom collecting system. Complete with frontal piping (heavy) and butterfly valves designed on 1.50 m / sec velocity.
| a) | Multi Grade Filter for Municipal Water Supply
Shell thickness : 8 mm.
Dished ends : 10 mm
HOS : 1500 mm
Dia of filter : 1000 mm or As per manufacturer
Filteration Capacity: 280 LPM
Filteration Raterate : 17500 ltr./hr./m2
Filter Media : Silex Quartz, (Multigrade) and Anthracite
Material of Construction: MSEP
Manhole size : 450/ 600 mm
|  | Working Pressure : 2 - 3.5 Kg/Sq.cm. | Each | 1
| b) | Multi Grade Filter for Rain Water
Shell thickness : 8 mm.
Dished ends : 10 mm
HOS : 1500 mm
Dia of filter : 1000 mm or As per manufacturer
Filteration Capacity: 210 LPM
Filteration Raterate : 17500 ltr./hr./m2
Filter Media : Silex Quartz, (Multigrade) and Anthracite
Material of Construction: MSEP
Manhole size : 450/ 600 mm
|  | Working Pressure : 2 - 3.5 Kg/Sq.cm. | Each | 1
| c) | Activated Carbon Filter for Municipal Water Supply
Shell thickness : 8 mm.
Dished ends : 10 mm
HOS : 1500 mm
Dia of filter : 1000 mm or As per manufacturer
Filteration Capacity: 280 LPM
Filteration Raterate : 17500 ltr./hr./m2
Filter Media : Activated carbon
Material of Construction: MSEP
Manhole size : 450/ 600 mm
|  | Working Pressure : 2 - 3.5 Kg/Sq.cm. | Each | 1
| d) | Activated Carbon Filter for Rain Water
Shell thickness : 8 mm.
Dished ends : 10 mm
HOS : 1500 mm
Dia of filter : 1000 mm or As per manufacturer
Filteration Capacity: 210 LPM
Filteration Raterate : 17500 ltr./hr./m2
Filter Media : Activated carbon
Material of Construction: MSEP
Manhole size : 450/ 600 mm
|  | Working Pressure : 2 - 3.5 Kg/Sq.cm. | Each | 1
| 8.05 | Supply, Installing, testing and commissioning of Automatic dosing system (for domestic water treatment plant) consisting of one HDPE tank of 200 litres capacity with a positive displacement diphragm dosing pump having variable flowrate of 0-6 lph. The motor shall be suitable for operation at 240 V/single phase/50 Hz. Supply. The pump shall be supplied complete with necessary polypropylene piping, valves, strainers, low level switch and injection fittings. The pump shall be speed & stroke control Asia LMI / equivalent make.
|  | The cost shall be inclusive of providing salt for the testing and operation of system before handover to the owner. | Set | 2
| 8.06 | Online Filter before RW Inlet into RW Tank
Supply, installation, testing and commissioning of online micron cartridge filter suitable for a flowrate of 50000 LPH to achieve particle filtration of less than 25 microns. The unit shall be supplied complete with inlet and outlet branches removal cap for replacement of element, inlet and outlet pressure indicators, isolation valves etc. (One for the pressure treatment & other for CIP system) MOC: Polypropylene -- 2 sets.
| a) | Suitable for 150 mm Pipa Dia | Set | 1
| 8.07 | Supply, Fixing Water softening system comprising MS fabricated FRP lined vertical softener internal rubberized lining or epoxy coating with 50mm dia face piping and multiport valves, butterfly valves, brine injection system complete, regeneration cycle of 8 hours and HDPE tank, pressure gauge at inlet, outlet and back wash (each with isolation cock), valves, fittings and water hardness testing kit & T 40 NA Resin depth should not be less than 800 mm and quantity should not be less than 2150 litres.
| a) | Softner for Municipal Water Supply
OBR : As per Vendor
Resin depth : As per Vendor
Shell thickness : 8 mm.
Dished ends : 10 mm
HOS : 2100 mm
Dia : As per Vendor
Capacity : 280 LPM
Inlet Hardness : 450 ppm
Outlet Hardness : < 25 ppm
Working Pressure : 2 - 3.5 Kg/Sq.cm.
|  | Test Pressure : 4.5 Kg/Sq.cm. | Set | 1
| 8.08 | Supply, Installation, testing and commissioning MS rubber lined brine tank fabricated with 5 mm thick MS plate and lined with 4 mm thick rubber duly tested by spark test and certified for proper lining including brine delivery pipes and complete in all respect as of vendor's detail.: | Each | 1
| 8.09 | Providing & fixing Full Way Lever operated Ball Valve with threaded / flanged joints complete with nuts, bolts, gaskets, washers etc.
MOC: Forged Brass, Nickel Plated, Full Bore
Ball: Forged brass Hard Chrome Plated mirror smooth finish with PTFE Seat
Handle: Dacromat rugged steel with PVC grip
Lever and Nut: Nyloc self-locking type
Stem Seals to be Double “O” Rings of H-NBR (Hydro Generated Nitrile Rubber)
Pressure Rating: PN20 or PN25
| a) | 32 mm dia | Each | 0
| b) | 40 mm dia | Each | 0
| c) | 50 mm dia | Each | 2
| 8.1 | Providing & fixing Butterfly valve complying to IS: 13095 and AWWA Standard (upto 150mm dia with hand lever operation & above with gear box operation) including rubber gasket, flanges, nuts, bolts, washers & painting complete as required.
Material of Construction:
Body: Graded Cast Iron duly powder coated
Disc: Ductile Iron Electro less Nickel plated / SS (304 & 316) having mirror smooth edges
Shaft: SS Single piece through shaft Spline design technology
Replaceable EPDM rubber sleeve with hard backing
Pressure Rating: PN20
| a) | 65 mm dia | Each | 10
| b) | 80 mm dia | Each | 10
| c) | 100 mm dia | Each | 0
| d) | 150 mm dia | Each | 0
| e) | 200 mm dia | Each | 8
| 8.11 | Providing & fixing Spring Loaded Uni directional Full Bore Forged brass Non return valve conforming to EN29000 - ISO 9000. The inner valve should be made of Hostaform having soft seating and NBR Rubber seat ring. The seat should lift easily and should have a conical tempered SS 316 spring. Pressure rating shall be PN20 or PN25 including rubber gasket, flanges, union, nuts, bolts & washers complete as required.
| a) | 25 mm dia | Each
| b) | 32 mm dia | Each | 0
| c) | 40 mm dia | Each | 0
| 8.12 | Providing & fixing Dual Plate Check valve (NRV) including rubber gasket, flanges, union, nuts, bolts, washers & painting complete as required.
Material of Construction:
Body: Cast Iron Powder Coated
Seat Ring: EPDM
Disc: Ductile Iron Electro less Nickel plated/SS (304)
Spring & Hinge Pin: SS 304 (CF 8)
Stem: SS 410
Washers: P.T.F.E
Pressure Rating: PN20
| a) | 50 mm dia | Each | 2
| b) | 65 mm dia | Each | 8
| c) | 80 mm dia | Each | 0
| d) | 100 mm dia | Each | 0
| e) | 150 mm dia | Each | 0
| 8.13 | Providing & fixing `Y' Strainer (screwed/flanged) with stainless steel fine wire mesh perforated sheet basket with necessary flange/ unions nuts, bolts and washers complete as required
Material of Construction:
Body: Cast Iron
Filter: SS
Pressure Rating: PN10
| a) | 40 mm dia | Each | 0
| b) | 50 mm dia | Each | 0
| c) | 65 mm dia | Each | 0
| d) | 80 mm dia | Each | 1
| e) | 100 mm dia | Each | 0
| f) | 150 mm dia | Each | 0
| g) | 200 mm dia | Each | 4
| 8.14 | Providing and fixing heavy duty floating flange EPDM rubber expansion joint with unit control (tie rod & gusset plate) as per manufacturers specifications of standard length complete with all accessories and a working pressure not less than 20 Kg./sqcm including rubber gaskets, flanges, nuts, bolts & washers complete as required.
| a) | 40 mm dia | Each | 0
| b) | 50 mm dia | Each | 2
| c) | 65 mm dia | Each | 10
| d) | 80 mm dia | Each | 8
| e) | 100 mm dia | Each | 0
| f) | 150 mm dia | Each | 0
| 8.15 | Providing and Fixing of Pressure Gauge as per the description below complete with all necessary connections
Burden type Stainless Steel dial type pressure gauge with brass isolation valve and pipe
Dial Diameter : 100 mm
|  | Caliberation : 0-10 Kg/cm2 | Each | 4
| 8.16 | Providing, fixing, jointing and testing in position the following heavy class GI pipes conforming to IS:1239 cut to required lengths including all necessary fittings (conforming to IS:1879) and specials such as bends, tees, unions, reducers, flanges & plugs etc. fixing at wall / ceiling level supported by clamps, hangers etc (to be galvanized after fabrication) cutting hole in wall / floor / slab and making good the same good with cement concrete 1:2:4 / fire sealent complete as required. All hangers, clamps, brackets etc. shall be of galvanized iron unless specified otherwire and then supply of the same shall also be included for rates under this head. All structural supports, Hangers, clamps etc. shall be inclusive with piping and shall be ETA Approved. (Location: Within Pump Rooms, 2 metres around each Sump Pit)
| a) | 32 mm dia | RM | 0
| b) | 40 mm dia | RM | 0
| c) | 50 mm dia | RM | 4
| d) | 65 mm dia | RM | 24
| e) | 80 mm dia | RM | 14
| f) | 100 mm dia | RM | 19.5
| g) | 150 mm dia | RM | 0
| h) | 200 mm dia | RM | 19.5
| 8.17 | Providing two coats of Synthetic enamel paint of approved shade on pipes and supports as per pipe colour code over a coat of primer. Including painting of legends with direction arrow as per the approval of the Consultants / Project Manager.
| a) | 32 mm dia | RM | 0
| b) | 40 mm dia | RM | 0
| c) | 50 mm dia | RM | 4
| d) | 65 mm dia | RM | 24
| e) | 80 mm dia | RM | 14
| f) | 100 mm dia | RM | 19.5
| g) | 150 mm dia | RM | 0
| h) | 200 mm dia | RM | 19.5
Note: All valves shall be of PN20 rating
| 8.18 | Providing and fixing C.I double flanged equilibrium float valve with M.S. lever high pressure, copper ball and flanges including nuts, bolts, 3mm thick rubber insertions complete (Underground fire tanks)
| a) | 65 mm dia | Each | 0
| b) | 80 mm dia | Each | 1
| c) | 100 mm dia | Each | 0
| 8.19 | Providing and fixing motorized butterfly valve with panel as per tower/rotary actuator (CI body, SS316 disc, EPDM boot seat, SS416 shaft, RPTEF bushing @PN20rating) for filling of overhead water tank complete with electrical water level control panel, including by-pass connection for the same dia with manually operated butterfly valve and all piping and accessories complete in all respects
(Up to 50mm dia solenoid valves can be considered and for 65mm & above motorised butterfly valves can be considered).
| a) | 50 mm dia - OH FWS Water Tank Inlet | Each | 1
| b) | 200 mm dia - UG Rain Water Tank Inlet | Each | 1
| c) | 65 mm dia - OH DWS Water Tank Inlet | Each | 1
| 8.2 | Providing, fixing and testing Water Flow Meters in C.I./brass body flanged at both ends with companion flanges, gaskets, bolts nuts and washers, with electronic digital type display for real time & totalized flow rate of water, with panel and cabinet, memory facility, flow switches and sensors and required accessories complete including cutting and making good the pipeline, and making all electrical connections. Water meters should be BMS compatible. pressure rating should be PN20. (With bypass arrangements with 3 valves).
| a) | 65 mm dia - Domestic Water | Each | 1
| b) | 200 mm dia - Rain Water & Sewer | Each | 2
| c) | 65 mm dia - Flushing+Irrigation Water | Each | 1
| 8.21 | Providing and fixing water meter with direct reading dial in KL with all internal parts in gunmetal or brass, strainer, flanged distance piece for easy removal in future, 80 mm dia. Bourden type pressure guage and isolation cock including necessary test certificate for the meter (For water supply metering from source). | Each | 1
| 8.22 | Providing and fixing complete electronic type PLC based level indicator cum controller for water tanks and pumps automation with mounting in panel with the following features, level display, alarm when water level is low or high, full range from one level to four level display and manual reset for Alarm, pump auto switch on/off etc. with electrical wiring conduit supports from wall & ceiling probes and all other accessories complete as required. | Lot | 1
| 8.23 | Control Cable:
|  | Supply and laying of 2C x 1.5 Sq.mm copper armoured cable including termination. (Control cable shall be paid separately under control cable head). | RM | 100
TOTAL CARRIED TO SUMMARY
| 9 | ELECTRICAL WORKS FOR PLUMBING SYSTEM
Design, manufacture, assembly, wiring, testing at works and supply to site of following electrical panels/distribution boards/switch boards. The boards shall be designed and fabricated as per general specifications, technical details, specifications and notes as part of this tender /BOQ and relevant BIS codes.
Also, refer to General Notes and Specifications for Panels/ Boards
GENERAL NOTES FOR MCCB's:
| a. | ACB's & MCCB's shall be of 3P or 4P as called for in the BOQ.
| b. | Ics = Icu = 100% for the MCCB's, MPCB's & ACB's
| c. | MCCB's shall be with extended rotary handle.
| d. | Exact rating (Amps), Poles, Type/Duty, Short circuit rating of MCCB is to be selected by the contractor as per load, fault and requirement and also approval taken.
Notes:
| 1 | All Switchgear selections shall be as per manufacturer's recommendation.
| 2 | Contractor to submit manufacturer's selection charts for approval.
| 3 | Only one make of switchgear to be used in a board /panel.
| 4 | All communicable meters should be looped inside the panels and this loop has to be brought to one terminal point in the panel for connectivity.
| 5 | No BMS cable should be directly connected to VFD and hence these points will have to brought on to the terminal blocks inside the panel.
| 6 | All energy meters shall be dual source and communicable type.
| 7.0a | EMC & RFI FILTRATION FOR VFD's.
VFD’s for sensitive installations where life critical data communications are of importance ,like: • Hospitals • Airports • Electronic Industry • Data centres • Communication centres These installations Must have ‘C1’ category of RFI & EMC filters for 50 meters of cable length. These are applicable to all the VFD’s of AHU’s, fans, blowers, pumps and cooling towers. For these above mentioned critical applications, if chiller motors and pump motors are more than 90Kw, then ‘C2’ category of filters to be used if ‘ C1’ is not available. VFD’s for normal buildings and others similar installations shall have ‘C3’ category of RFI & EMC filter for AHU’s , fans, blowers, pumps, cooling towers & Chillers .
| 7.0b. | THDI for VFD's between 35% and 40% .
| 8 | All VFD's shall be IP-20, if installed inside the panels and shall be IP55 if installed without enclosure.
| 9 | Incomer switchgear, bus bars, supports and outgoing switchgear shall be of same fault level withstand capacity as mentioned for the panel.
| 10 | All starter feeder / VFD feeder in panels means complete with starter & VFD as the case may be as per specifications.
| 11 | In the Motor Control Panel & Other Panels : It is recommend not to have 230V supply on panel door for Metering & Indication lamps. Therefore 415/√3 / 110 / √3 PT is considered to get 110 / √3 for ( 3 nos. Single phase PT's) for: ● R, Y, B Phase indication lamp at the incomer : 63V ● Incomer Metering / MFM meters:110V incomer metering ● On, Off, Trip indication lamps at incomer: 110V
| 12 | In the Motor Control Panel & Other Panels: It is also recommended to have a control transformer 415V (2 Phase) / 110V (1 Phase) for: • Starter's contactor coil (110V) • ON, OFF, Trip Indication lamps of outgoing starter feeders / feeders(110V) • A 110V control bus to run inside the panel.
| 13 | For Motor Control Centres & Other Panels, provide:
Incomer Metering Chamber:
• Provide a Separate Metering Chamber for the Incomer to house a 415V / √3 / 110V / √3 PT.
• Door to have R, Y, B (63.5V) LED indication lamp for incomer.
• Door to have VAF / Metering (110V) incomer metering.
• Door to have ON, OFF, Trip Indication for incomer (110V).
Control Transformer Chamber:
Provide a separate Control Transformer Chamber to house a 415V (2 Phase) / 110V (1 Phase) Control Transformer for outgoing feeders for:
• ON / OFF / Trip Indication (110V) for out going feeders.
• Starter / Contactor Coils (110V) for out going feeders.
| 14 | GENERAL NOTES FOR TRANSIENT VOLTAGE SURGE SUPPRESSOR (TVSS):
| a. | Transient Voltage Surge Suppressors (TVSS) shall be mounted out side the panel / switch board in a sheet steel enclosure.
| b. | It shall be suitable for handling required (specified) surge handling capacity, shall be 10 modes protection with noise filters. (EMI & RFI) and with inbuilt back up fuse protection.
| c. | Surge suppressor shall be complete with isolating / protective device in the form of MCB / MCCB of KA rating (breaking capacity) as of switch board.
| 9.01 | PLUMBING PANEL-1 (IN PHE PLANT ROOM)
IP Rating : IP 54
Short Circuit Fault with stand Capacity: 10KA
Incomer:
• 1 No. 100A, 3P, MCCB with Micro processor based Thermal & Magnetic adjustable releases and suitable rating as per load & duty.
• MCCB with 2NO + 2NC contacts and an auxiliary trip contact with additional trip contact multiplier for BMS.
Incomer Indications:
• R,Y,B phase indication lamps: 63V
• ON/OFF, Trip indication lamps: 110V
• Indication lamps shall be LED type
Incomer Metering:
• 1 No. combined Digital VAF meter
• Meter shall be (110V) and communicable type.
CT for Incomer Metering :
• CT metering Class-1 accuracy CT’s (one per phase)
• CT shall be cast resin type & shall be of suitable burden (VA) & ratio.
PT for Incomer Metering & Indication Lamps:
• 415V / √3 / 110V / √3 PT for metering and indication lamps. (3 Nos. 1 Phase PT's)
• PT shall be Class-1 accuracy.
• PT shall be cast resin type.
• PT shall be of suitable burden (VA).
Protection for Metering PT:
• TP MPCB of suitable rating & of fault withstand capacity as of panel on primary side of PT.
• TP MCB of suitable rating on secondary side of PT.
Bus Bars:
• 150A, 3P, Aluminium Bus Bars of electrolytic grade with heat shrinkable sleeves.
110V Control Transformer for Contactor Coils of Starters & out goings Indication lamps & VFD Cooling fans:
• 1 No. 415V / 110 V, cast resin control transformer. (2 Phase Input/ 1 Phase, 110V Output)
• Transformer to be of adequate burden.
• Transformer with primary taps at ± 2.5%, ±5%, 50HZ.
• 110V control bus.
• TP MPCB of suitable rating & fault withstand capacity as of panel at Primary side & DP MCB at secondary side of each control transformer.
Outgoings
DOL Starter Feeders for:
1 No. 2.98 KW for Filter Feed Pump
1 No. 2.24 KW for Rain Water Filter Feed
1 Nos. 3.73 KW for Domestic OHT Filling Pump
1 Nos. 3.73 KW for Flushing OHT Filling Pump
1 No. 1.12 KW for Irrigation Pump
Spare DOL Starter Feeders:
1 No. 3.73 KW
1 No. 5.6 KW
Feeder for Basement Car Parking Drainage Sump Pump Panels (sumps in basement and elsewhere) (without starter): No. of feeders - 2
• 3 No. 3P, MPCB of suitable rating as per load of Panel of 7.5 kW (total load of both sump pumps working).
• MPCB shall be with inbuilt thermal & magnetic releases.
• MPCB with 1NO + 1NC contacts and an auxiliary trip contact for BMS.
• ON / OFF / TRIP Indication lamps LED type 110 V.
• Digital Ammeter.
• 3 Nos. metering Class 1 accuracy cast resin CT's of suitable ratio & burden.
Feeder for Basement Sewerage Sump Pump Panels (sumps in basement and elsewhere) (without starter): No. of feeders - 1
• 1 No. 3P, Thermal Magnetic MCCB of suitable rating as per load of panel of 4.5 kW
• MCCB shall be with fixed thermal & magnetic releases.
• MCCB with 2NO + 2NC contacts and an auxiliary trip contact with additional trip contact multiplier for BMS.
• ON / OFF / TRIP Indication lamps LED type 110 V.
• Digital Ammeter.
• 3 Nos. metering Class 1 accuracy cast resin CT's of suitable ratio & burden.
Feeder for Pump Room Sump Pump Panels (sumps in basement and elsewhere) (without starter): No. of feeders - 1
• 1 No. 3P, Thermal Magnetic MCCB of suitable rating as per load of panel of 3.0 kW
• MCCB shall be with fixed thermal & magnetic releases.
• MCCB with 2NO + 2NC contacts and an auxiliary trip contact with additional trip contact multiplier for BMS.
• ON / OFF / TRIP Indication lamps LED type 110 V.
• Digital Ammeter.
• 3 Nos. metering Class 1 accuracy cast resin CT's of suitable ratio & burden.
Feeder for Domestic Terrace Booster Pump Panels (sumps in basement and elsewhere) (without starter): No. of feeders - 1
• 1 No. 3P, Thermal Magnetic MCCB of suitable rating as per load of panel of 3.0 kW
• MCCB shall be with fixed thermal & magnetic releases.
• MCCB with 2NO + 2NC contacts and an auxiliary trip contact with additional trip contact multiplier for BMS.
• ON / OFF / TRIP Indication lamps LED type 110 V.
• Digital Ammeter.
• 3 Nos. metering Class 1 accuracy cast resin CT's of suitable ratio & burden.
Feeder for Flushing Terrace Booster Pump Panels (sumps in basement and elsewhere) (without starter): No. of feeders - 1
• 1 No. 3P, Thermal Magnetic MCCB of suitable rating as per load of panel of 3.0 kW
• MCCB shall be with fixed thermal & magnetic releases.
• MCCB with 2NO + 2NC contacts and an auxiliary trip contact with additional trip contact multiplier for BMS.
• ON / OFF / TRIP Indication lamps LED type 110 V.
• Digital Ammeter.
• 3 Nos. metering Class 1 accuracy cast resin CT's of suitable ratio & burden.
Spare Feeder (without starter): No. of feeders - 1
• 1 No. 3P, Thermal Magnetic MCCB of suitable rating as per load of panel of 7.5 kW
• MCCB shall be with fixed thermal & magnetic releases.
• MCCB with 2NO + 2NC contacts and an auxiliary trip contact with additional trip contact multiplier for BMS.
• ON / OFF / TRIP Indication lamps LED type 110 V.
• Digital Ammeter.
• 3 Nos. metering Class 1 accuracy cast resin CT's of suitable ratio & burden.
Important Notes:
1. All incomer feeders, outgoing motor feeders, other feeders and bus bars shall be of the same fault withstand capacity as panel fault.
2. All Starter feeders for DOL, Star-Delta and Soft Starter shall be complete with and inclusive of the following:
DOL starter feeder upto 7.5 KW / 10HP Motor shall be complete with and inclusive of the following, but refer specifications for details:
● TP MPCB with in built Thermal & Magnetic releases.
● MPCB shall be Microprocessor based with adjustable O/L trip class.
● 3 Pole Contactor (110 V contactor coil voltage).
● A/M selector switch- 2pole/2way (for BMS connectivity)
● ON / OFF Push buttons
● ON /OFF / Trip indications (110V) (ON /OFF Indication from contactor's 2NO / 2NC Aux. Contacts & trip indication from MPCB Aux. contact) with additional trip contact multiplier for BMS.
● Digital Ammeter with inbuilt selector switch and with metering class CT's (Upto 10 HP, only one CT in one of the phases)
● Internal wiring
● Type-II coordination
|  | Plumbing Panel as described above. | Set | 1
| 9.02 | LT CABLES, SUB MAINS CABLING
The rate shall also include the following:
| 1 | Effecting adequate and proper connections at terminations.
| 2 | Providing all fixing accessories such as clamping devices nuts, bolts and screws.
| 3 | Wherever the cables are of aluminum and bus bars of copper bimetallic lugs shall be used.
| 4 | All cable shall be laid with one diameter gap or as specified or as called for.
| 5 | All cable shall be IS approved.
| 6 | Fire retardent paint one meter on both side of wall penetration and at termination as per specifications.
| 7 | Burried LT cables to be laid atleast 750mm below ground.
| 8 | All cutouts / sleeves shall be sealed with fire retardant sealent as approved.
| 9 | Leave sufficient cable loops at both the cable ends.
| 10 | Use Tinned copper thimbles/lugs with copper cables/copper wires.
| 11 | Cable Clamps, saddles & screws :
| 12.1 | Cable fixing clamps, saddles & screws on trays / walls / slabs
Indoor Application:
· Aluminium
· Readymade type of clamps or Made from 20mm x 3mm aluminium sheet / strips.
· 8mm SS-304 Screws for cable size 90mm² and above.
· 6mm SS-304 Screws for cable size less than 90mm².
Outdoor Application:
· SS-304
· Made from 20x1.8mm SS-304 sheet / strips.
· 8mm SS-304 Screws for cable size 90mm² and above.
· 6mm SS-304 Screws for cable size less than 90mm².
| 12.2 | Clamps spacing
· 600mm C/C in vertical fashion in shaft on vertical trays.
· 1000mm C/C on horizontal tray or cable racks.
| 2A. | SUPPLY OF CABLES - XLPE INSULATED, FR-LSH PVC SHEATHED COPPER CONDUCTOR ARMOURED CABLES (IS:7098 Part-I)
Supply of following sizes of 1.1kV grade XLPE insulated, Extruded FR-LSH PVC inner sheath Type ST-2, FR-LSH PVC outer sheath Type ST-2, stranded Copper conductor, Armoured cables as per IS:7098 Part-I.
3 CORES - ARMOURED (MAY BE USED FOR PLUMBING PUMPS, MOTORS & OTHERS)
| i. | 3C x 4 sq.mm.Cu. Ar. XLPE cable | RM | 110
| ii. | 3C x 6 sq.mm.Cu. Ar. XLPE cable | RM | 90
| iii. | 3C x 10 sq.mm.Cu. Ar. XLPE cable | RM | 380
| 2B. | LAYING OF CABLES- ON EXISTING TRAYS / IN EXISTING DUCTS / IN EXISTING CIVIL TRENCHES (IS:7098 Part-I)
Laying, Fixing, Testing & Commissioning of following sizes of 1.1kV grade XLPE insulated, Extruded FR-LSH PVC inner sheath Type ST-2, FR-LSH PVC outer sheath Type ST-2, stranded Copper conductor, Armoured cables as per IS:7098 Part-I on existing cable trays/ in existing hume pipes/ PVC pipes/ GI pipes/on surface of slabs, walls or masonary/ RCC trenches/ ducts including Aluminum/SS 304 clamps with SS screws and necessary hard ware.
3 CORES - ARMOURED
| i. | 3C x 4 sq.mm.Cu. Ar. XLPE cable | RM | 110
| ii. | 3C x 6 sq.mm.Cu. Ar. XLPE cable | RM | 90
| iii. | 3C x 10 sq.mm.Cu. Ar. XLPE cable | RM | 380
| 2C. | CABLE TERMINATION (IS:7098 Part-I)
Cable end Termination of following sizes 1.1kV grade XLPE insulated, Extruded FR-LSH PVC inner sheath Type ST-2, FR-LSH PVC outer sheath Type ST-2, stranded Copper conductor, Armoured cables as per IS:7098 Part-I including cost of tinned copper, heavy duty crimpping lugs, double compression glands, insulation tape and all necessary material to complete the termination.
3 CORES - ARMOURED
| i. | 3C x 4 sq.mm.Cu. Ar. XLPE cable | Nos. | 14
| ii. | 3C x 6 sq.mm.Cu. Ar. XLPE cable | Nos. | 6
| iii. | 3C x 10 sq.mm.Cu. Ar. XLPE cable | Nos. | 8
| 3 | Control Cable:
| a. | Supply and laying of 3C x 1.5 Sq.mm copper armoured cable including termination. (Control cable shall be paid separately under control cable head). | RM | 75
| b | Providing and fixing 25mm x 5mm G.I strip in 40mm dia G.I pipe from earth electrode including connection with G.I nut, bolt, spring, washer excavation and re-filling etc. as required. | RM | 75
| 4 | Supply and Erecting of LADDER type Hot dip G.I. cable tray of 14G of specific dimensions. The cable tray shall be hung from ceiling / fixed to wall with necessary ceiling suspensors, tee, nots, nuts etc, together with tees, bends etc including cost for supports as described. The tray shall be earthed. Min size (not a limitation) of supports shall be as follows (a).-up to 300mm tray 2nos. 8mm full threaded G.i. rod with 2nos.anchor fastner and "C" channel support at 500mm distance (b) 450 to 600mm tray 2nos.10mm full treaded G.I. rodwith 2nos. anchor fastner and "C" channel support at 500mm distance (c) 750 / 1000 mm cable tray with fabrication of 25 x 6 or 50 x 3 mm angle frame with min. 4 nos anchor fastner at 500 mm distance. (Size shall be 300mmX 50mm) | RM | 50
TOTAL CARRIED TO SUMMARY

## Summary-Sanitary (hidden)
SUMMARY OF COST
FOR PLUMBING WORKS OF ADMIN BLOCK FOR GALGOTIAS UNIVERSITY AT GREATER NOIDA
S No. | Description | Amount
1 | SANITARY FIXTURES & C.P. FITTINGS (Supply only) | 32678265
| GRAND TOTAL | 32678265
NOTE: | GST SHALL BE EXTRA AS APPLICABLE

## Boq sanitary fix. supply only (hidden)
SCHEDULE OF QUANTITIES
FOR SUPPLY FIXTURES OF GODREJ GCR, GURUGRAM
Sl. No. | Description | Unit | Total Qty. | Rate (Rs.) | Amount (Rs.) | Remark
PREAMBLE
1 | All items of work under this Contract shall be executed strictly to fulfill the requirements laid down under “Basis of Design” in the specifications. Type of equipment, material specification, methods of installation and testing and type of control shall be in accordance with the specifications, approved shop drawings and the relevant Indian Standards, however capacity of each component and their quantities shall be such as to fulfill the above mentioned requirement.
2 | The unit rate for all equipment or materials shall include cost in INDIAN RUPEES (INR) for equipment and materials including all taxes and duties and also including forwarding, freight, insurance and transport,loading unloading, housekeeping, safety and security into Contractor’s store at site, storage, installation, testing, balancing, commissioning and other works required.
3 | The rate for each item of work included in the Schedule of Quantities shall, unless expressly stated otherwise, include cost of:
a. All materials, fixing materials, accessories, appliances tools, plants, equipment, transport, labour and incidentals required in preparation for and in the full and entire execution, testing, balancing, commissioning and completion of work called for in the item and as per Specifications and Drawings.
b. Wastage on materials and labour.
c. Loading, transporting, unloading, handling/double handling, hoisting to all levels, setting, fitting and fixing in position, protecting, disposal of debris and all other labour necessary in and for the full and entire execution and for the job in accordance with the contract documents, good practice and recognized principles.
d. Liabilities, obligations and risks arising out of Conditions of Contract.
e. All requirements of Specifications, whether such requirements are mentioned in the item or not. The Specifications and Drawings where available, are to be read as complimentary to and part of the Bill of Quantities and any work called for in one shall be taken as required for all.
f. In the event of conflict between Bill of Quantities and other documents including the Specifications, the most stringent shall apply. The interpretation of the Architect / Consultant /Project Manager shall be final and binding.
4 | The Contractor shall procure and bring Materials/Equipment to the site only on the basis of drawings approved for construction and shop drawings and not on the basis of Bill of Quantities which are approximate only. This also applies to the Contractor’s requisition for Owner supplied materials. Quantity indicated in BOQ are estimated quantity. Vendor / Contractor carry out the actual measurement at site and submit schedule to take permission from PMC / Client Project Manager before procurement. This contract will be operated on unit rate basis and payment shall be made as per actual erected quantity at site.
5 | The contractor shall include for making all the opening in slabs, beams, walls etc. as required for his work. However, the contractor can coordinate with civil work to provide necessary sleeves. All openings shall be closed using water proofing compound or as specified by Project Manager. G.I. pipe sleeve of suitable higher size shall be provided wherever the pipes are crossing the walls/floors and sealing the sleeves with glass wool in between & fire sealant compound at either end.
6 | The work shall be carried out in conformity with the plumbing drawings and within the requirements of architectural, HVAC, electrical structural and other specialized services drawings.
7 | The contractor shall cooperate with all trades and agencies working on the site. He shall make provision for hangers, sleeves, structural openings and other requirements well in advance to prevent hold up of progress of the construction schedule. All supports to the civil structure shall be provided with anchor fastners.
8 | On award of the work, contractor shall submit a schedule of construction in the form of a PERT chart or BAR chart for approval of the Project Manager. Along with schedule contractor to submit Project Team and their hierarchy chart, cash flow, shop drawing submittal and approval schedule, equipments and material technical data sheet schedule, material delivery schedule, manopower deployment schedule.
9 | On award of the work the contractor shall be issued two (2) sets of consultant’s drawings. The drawings shall be the basis of contractor’s shop drawings.
10 | Shop drawings are detailed working drawings coordinated with other trading work, which incorporate the contractor’s details for execution of the work and incorporate equipment manufacturer’s details and dimensions to ensure that the same can be installed in the space provided.
11 | All shop drawings should detail pipe routing and levels, showing location of other services at crossings etc., cable runs, route cable trays and all allied works and must be fully coordinated with other services, before execution of the works.
12 | All shop drawings will be made on Autocad and coloured prints has to be produced for site work.
13 | All rates quoted are inclusive of cutting holes and chases in walls and floors with core cutting machines ans electrical chasing machines and making good the same with cement mortar / concrete / water proofing of appropriate mix and strength as directed by the Project Manager. Contractor shall provide holes, sleeves, recesses in the concrete and masonry work as the work proceeds. All hot and cold water supply pipes crossing masonry walls of typical guest room toilets shall be provided with GI pipe sleeves. The annular space between the pipe and sleeve shall be filled up with glass wool in between and fire proof sealent on either end after testing.
14 | Any pipe crossing fire rated wall as per fire compartmentation will be provide with higher size of GI sleeve. All floor crossing pipes will be provided with higher size GI sleeve.
15 | The contractor shall , from time to time, clear away all debris and excess materials accumulated at the site failing which the same shall be done by Project Manager at contractor’s risk and cost and cost of clean up shall be deducted from the contractors prorata bill.
16 | After the fixtures, equipment and appliances have been installed and commissioned, contractor shall cleanup the same and remove all plaster, paints, stains, stickers and other foreign matter or discoloration leaving the same in a ready to use condition.
17 | On completion of all works, contractor shall demolish all stores, remove all surplus materials and leave the site in a broom clean condition, failing which the same shall be done by the Project Manager at the Contractor'’ risk and cost. Cost of the cleanup shall be deducted from the contractor’s bills on pro-rata basis in proportion to his contact value.
18 | Contractor shall furnish sample of materials such as pipe, union, elbow, support (angle, hanger, rod, etc.), fittings, accesssories, sealant, cable trays, switches, sockets, etc. proposed for the project for Engineer's / PMC / Project Manager / Architect's approval before procurement / installation.
19 | The Contractor / Tenderer should quote rates based on the first approved make of each item in the List of Approved Makes attached with the technical specifications of this tenderer OR specify the make which is quoted.
20 | The rates quoted shall also include submission and approval of shop drawings, As-built drawings, Technical Data Sheet, Inspection, factory inspection,Testing and Commissioning
21 | Rate should include to follow Client / Godrej compliances such as Safety, Security of vendor store and material, regular housekeeping, etc. Dedicate resource to consider.
22 | Contractor shall list here any other items not included but necessary for the complete and satisfactory completion of each section of the work. Such items shall deemed to be included in other rates unless specifically listed here.
1 | SANITARY FIXTURES & C.P. FITTINGS (Supply only)
1.01 (a) | Supply of wall hung type white vitreous china European water closet with concealed `P' or ‘S’ trap, seat & lid (heavy duty) C.P. brass hinges, including C.I. chair, with chair grouting, rubber buffers, C.P. nuts, bolts, accessories etc. (For Typical Toilets ground to 19M) | Each | 479 | 13050 | 6250950
Option-1, Make: Toto, Model: CW822RA-Avante wall hung toilet TX215C-Slip in Connector TC281SJ-Duroplast Seat & Cover W/Metal Hinges & Soft Closing (Elongated)
Option-2, Make: Kohlar, Model: 27902IN-SS-0 ModernLife Edge True Rimless toilet
1.01 (b) | Supply of wall hung type white vitreous china European water closet with concealed `P' or ‘S’ trap, seat & lid (heavy duty) C.P. brass hinges, including C.I. chair, with chair grouting, rubber buffers, C.P. nuts, bolts, accessories etc. (For Other areas Toilets of Basements ground & L-1) | Each | 39 | 9135 | 356265
Make & Model as per Client / Architect
1.02 (a) | Supply of concealed in wall flushing cisterns with flushing actuator plate.(For Typical Toilets ground to 19M) | Each | 479 | 7200 | 3448800
Option-1, Make: Toto, Flushing tank-WH132MNF 3-4.5 LITRES, Flush Plate- MB003CPR-2
Option-2, Make: Kohlar, Model: Flushing tank-77028IN-M-NA INSTAFIT+ MECHANICAL, Flush Plate- 8857IN-M-CP BEVEL
1.02 (b) | Supply of concealed in wall flushing cisterns with flushing actuator plate. (For Other areas Toilets of Basements ground & L-1) | Each | 39 | 5040 | 196560
Make & Model as per Client / Architect
1.03 (a) | Supply of white glazed vitreous China wash basin undercounter with 32 mm dia C.P brass waste of standard pattern, 32 mm dia C.P cast brass bottle trap and union, 32 mm dia C.P brass pipe to wall and CP wall flange, and rubber acceptors for waste connection.
| Wash basin undercounter (For Typical Toilets ground to 19M) | Each | 426 | 3150 | 1341900
Option-1, Make: Toto, Model: L520E#W -Rectangular Under Counter Lavatory 604W X 365D, Popup waste: T6JV6, Bottle trap:THX1A 3N
Option-2, Make: Kohlar, Model: Ladena Undercounter, Popup waste: 27902IN-SS-0 ModernLife Edge True Rimless toilet, Bottle trap:75823IN-CP
1.03 (b) | Supply of white glazed vitreous China wash basin undercounter with 32 mm dia C.P brass waste of standard pattern, 32 mm dia C.P cast brass bottle trap and union, 32 mm dia C.P brass pipe to wall and CP wall flange, and rubber acceptors for waste connection.
| Wash basin undercounter (For Other areas Toilets of Basements ground & L-1) | Each | 47 | 2205 | 103635
Make & Model as per Client / Architect
1.04 (a) | Supply of 15mm dia C.P. pillar tap for wash basin. (For Typical Toilets ground to 19M) | Each | 426 | 7425 | 3163050
Option-1, Make: Toto, Model: SENSOR TAP - TEN12ANV900
Option-2, Make: Kohlar, Model: SENSOR TAP - 18656IN-ND-CP
1.04 (b) | Supply of 15mm dia C.P. pillar tap for wash basin. (For Other areas Toilets of Basements ground & L-1) | Each | 47 | 5197.5 | 244282.5
Make & Model as per Client / Architect
1.05 (a) | Supply of white glazed vitreous china large flat back lipped front urinal basin, C.I bracket (white colour painted) 40 mm CP brass domical waste, 40 mm C.P. caste brass bottle trap, CP flush pipe with spreader & other necessary fittings including C.P. brass hex nipple; elbow; unions, washers, cap, C.P. nuts, bolts etc making holes in walls, floors & making good.
| Urinal - Flat back (For Typical Toilets ground to 19M) | Each | 252 | 13500 | 3402000
Option-1, Make: Toto, Model: U904VM (BACK INLET)
Option-2, Make: Kohlar, Model: 18645IN-SS-0 Patio Urinal
1.05 (b) | Supply of white glazed vitreous china large flat back lipped front urinal basin, C.I bracket (white colour painted) 40 mm CP brass domical waste, 40 mm C.P. caste brass bottle trap, CP flush pipe with spreader & other necessary fittings including C.P. brass hex nipple; elbow; unions, washers, cap, C.P. nuts, bolts etc making holes in walls, floors & making good.
| Urinal - Flat back (For Other areas Toilets of Basements ground & L-1) | Each | 9 | 9450 | 85050
Make & Model as per Client / Architect
1.06 (a) | Supply of Infra-Red based electronic urinal flushing system operated on 6V DC (4AA) battery for urinals comprising of solenoid valve, concealed built in strainer & flow mechanism piping, flush mounted sensors with all accessories & fittings complete in all respect in fully operational condition etc including cutting and making good the wall where required. (For Typical Toilets ground to 19M) | Each | 252 | 15750 | 3969000
Option-1, Make: Toto, Model: DUE126UPE
Option-2, Make: Kohlar, Model: 24199IN-C03-CP Patio Urinal Sensor With AC Adaptor (AC + DC)
1.06 (a) | Supply of Infra-Red based electronic urinal flushing system operated on 6V DC (4AA) battery for urinals comprising of solenoid valve, concealed built in strainer & flow mechanism piping, flush mounted sensors with all accessories & fittings complete in all respect in fully operational condition etc including cutting and making good the wall where required. (For Other areas Toilets of Basements ground & L-1) | Each | 9 | 11025 | 99225
Make & Model as per Client / Architect
1.07 | Supply of white glazed vitreous china urinal partitions of approved make including rawl plugs, screws or any other approved device for Fixing arrangements, making holes in walls, floors & making good.
a) | Size 680 mm x 300 mm. | Each | 261 | 2000 | 522000
Option-1, Make: Toto
Option-2, Make: Kohlar
1.08 | Supply of Stainless steel kitchen sink with R.S. or CI bracket (painted white), 40 mm dia C.P. brass waste of standard pattern, C.P. brass chain and rubber, 40 mm dia caste brass bottle trap with necessary union, C.P. pipe to wall & CP wall flange complete with cutting and making good the walls where required Including all accessories require to fix the sink in granite or given platform and sealing side for leak proof complete.
a) | Single bowl with single drain board. | Each | RO |  | 0
Single bowl without drainboard (Make: Jayna, Model:Galexy, Cat no.SBFB 02, Bowl size 428 X 380 X 200mm anti scatch)
1.09 | Supply of Wall Mounted C.P. Brass Sink Mixer single hole / single lever with swinging casted spout of required size including cutting and making good the wall wherever required. | Each | RO |  | 0
Option-1, Make: Toto
Option-2, Make: Kohlar
1.1 | Supply of C. P. Brass single lever concealed Shower mixer 15 mm C.P brass spout & wall flange (for shower) including necessary fittings/ accessories, cutting & making good the wall wherever required. (For Other areas Toilets of Basements ground & L-1) | Each | 16 | 12000 | 192000
Option-1, Make: Toto
Option-2, Make: Kohlar
1.11 | Supply of revolving type shower head & shower arm (discharging multiple type of sets) including cutting and making good the walls / floors wherever required. (For Other areas Toilets of Basements ground & L-1)
a) | 1 No. Shower Head | Each | 16 | 3500 | 56000
b) | 1 No. shower arm incl. necessary fittings/accessories, cutting and making good the wall . | Each | 16 | 2000 | 32000
Option-1, Make: Toto
Option-2, Make: Kohlar
1.12 | Supply of stainless steel toilet paper holder of approved makes. Including cutting hole in the masonry/R.C.C wall and making good with cement mortar.
a) | Size 150 mm x 150 mm | Each | 518 | 825 | 427350
Option-1, Make: Toto, Model: YH406RC
Option-2, Make: Kohlar, Model: 5633IN
1.13 | Supply of CP brass coat hooks (double) of approved make. Including providing & fixing C.P brass screws, washers, rawl plug etc. | Each | 518 | 660 | 341880
Option-1, Make: Toto
Option-2, Make: Kohlar
1.14 | Supply of liquid soap dispenser of approved make. Including screws, washers and rawl plug etc. | Each | 473 | 3025 | 1430825
Make: BOBRICK, Model: Countertop Liquid Soap Dispenser (Vol. 1 Ltr., Spout 6") Model no-B 8226 HSN CODE-73249000
1.15 | Supply of CP brass short/long body bib cock including, necessary flange, cutting and making good he walls / floors wherever required complete. | Each | 124 | 1575 | 195300
Option-1, Make: Toto
Option-2, Make: Kohlar
1.16 | Supply of 15 mm dia C. P. Brass angle valve with C.P. copper connecting pipe , 450 mm long and nuts & washer with C.P. Brass flange complete including cutting and making good the Walls / Floors wherever required. | Each | 1073 | 412.5 | 442612.5
Option-1, Make: Toto, Model: WH131MNF Concealed Tank w/o Frame (6L/3L)
Option-2, Make: Kohlar, Model: 80158IN-9-CP
1.17 | Supply of CP brass towel ring of size 150 mm dia with screw and rawl plug etc, including cutting and making good the Walls / Floors wherever required. | Each | 473 | 2200 | 1040600
Option-1, Make: Toto
Option-2, Make: Kohlar
1.18 | Supply of CP brass air purifier holder fixed to PVC rubber plug with C.P brass screw complete each. | Each | 518 | 2250 | 1165500
Option-1, Make: Toto
Option-2, Make: Kohlar
1.19 | Supply of CP towel rod with CP brass bracket of approved make fixed to PVC rawl plug with CP brass screws, making holes in walls & making good the same. | Each | RO | 1375 | 0
Option-1, Make: Toto
Option-2, Make: Kohlar
1.2 | Supply of C.P. brass Ablution health faucet assembly comprising hand held shower with 8 mm dia flexible tube with mounting bracket fixed on wall complete. | Each | 518 | 1575 | 815850
Option-1, Make: Toto, Model: THX20MCRB Shower Spray,Chrome. 4.0 LPM (GREEN ITEM)
Option-2, Make: Kohlar, Model: 12927IN-CP COMPLEMENTARY - Health Faucet W/SDSpray, Metal Hose
1.21 | Supply of fully automatic "NO TOUCH" stainless steel finish hand drier suitable to operate on 220 volts, single phase 50 hz, A.C. power supply and directly plugged to power point complete. complete. | Each | 154 | 12325 | 1898050
Make: EURONICS, Model: EH26NW
1.22 | Supply of Grab Bar swing wall mount type for handicaped toilet including all accessories, cp screws etc. complete in all respect. | Each | 164 | 5695 | 933980
Make: EURONICS, Model: EGRS02
1.23 | Supply of Grab Bar straight handrail type for handicaped toilet including all accessories, cp screws etc. complete in all respect. | Each | RO | 1445 | 0
Make: EURONICS, Model: EGRO1
1.24 | Supply of Paper towel dispenser of approved model & make complete in all respects. | Each | 154 | 3400 | 523600
Make: EURONICS, Model: EPO2S
| Sub of Total subhead above CO to Summary |  |  |  | 32678265